## Cover Page & Notes
Washington State Department of Health
Conventional Water Treatment Plant and SWTR Disinfection Monthly Report Forms
Notes and Instructions
Version 1.0
Report Designed for All Water Systems
[5 empty] | Revision Date | 2006-03-17
Notes:
This Excel Workbook was developed by Washington State Department of Health, Office of Drinking Water.
This workbook was developed using Microsoft Excel 2000. However, it can be used in Excel 97 as well as later versions with no problems.
The workbook is intended for use by water treatment plant operators to enhance recordkeeping, reporting and legibility.
It is designed to minimize the work necessary to calculate totals, averages, count events, etc.
The SWTR Disinfection Monthly Reports will also look up and calculate required CT values for Giardia inactivation.
Data or calculations that do not comply with standards or requirements will show up in bold red.
Saving and Using this Workbook as a Template (Optional)
To save this workbook as a template, apply the following procedure:
Clear out any data input by the user.
Click on File, Save As. When prompted, give it a new file name, and specify the "Save as type" as Template.
Click on Save in the dialog box.
To use as template when starting a new month, use the following procedure:
With Microsoft Excel running, click on File, New. The WTP template should show in the "New" dialog box.
Click on the template; it will come up as a regular Excel spreadsheet.
When the spreadsheet is saved for the first time, you will be required to supply a name for the file.
Recommended file name: "WTP_<PWSID>_<Plant ID>_YYMM.xls", where YYMM is the reporting year and month; e.g.: WTP_00050_001_0308.xls.
The advantage of starting a workbook using a template is that you'll always have a blank workbook (without having to clear out an old one)
and minimize the chance of overwriting a previous month's workbook.
The Forms
The workbook consists of three forms, which are described below:
The WTP Monthly Rept (DOH Form #331-023) is for recording information on the operation of a conventional water treatment plant.
The SWTR Monthly Disinfection Rept (DOH Form #331-048) is for recording disinfection process information for a plant using Chlorine disinfection.
The Monthly Summary (DOH Form #331-172) gathers data from the other two forms, plus other provided information and reports
the SWTR compliance status for the month.
Entering Data:
All cells in the workbook are protected, except for those intended for data input by the user.
Cells and columns intended for user input have titles or headings colored blue.
Printing
Because of the size of the WTP Monthly Rept, it should be printed on legal size paper, in landscape mode, if it is desired to fit on one page.
Use the "Page Setup" menu to choose the paper size and orientation. Change left and right margins to 0.5" and check "Fit to" 1 pg wide by 1 pg tall.
The SWTR Monthly Disinfection Rept and the Monthly Summary each fit on letter size paper in landscape mode.
Where to Send these Report Forms
Send your report forms to the appropriate Office of Drinking Water regional office or as checked below:
|  | Northwest Drinking Water |  |  |  | Southwest Drinking Water | Eastern Drinking Water
|  | Operations |  |  |  | Operations | Operations
|  | Department of Health |  |  |  | Department of Health | Department of Health
|  | 20435 72nd Ave S., Ste 200 |  |  |  | P O Box 47823 | 1500 W. Fourth Ave, Ste 305
|  | Kent, WA 98032-2358 |  |  |  | Olympia, WA 98504-7823 | Spokane, WA 99240
|  | (253) 395-6750 |  |  |  | (360) 664-0768 | (509) 456-3115
For Persons with Disabilities
This document is available on request in other formats. To submit a request, please call 1-800-525-0127 (TTY 1-800-833-6388).
DOH Contact
If there are any questions, or if you find any errors in the workbook, please contact the following:
Simon T Tung, P.E.
Washington State Department of Health
Office of Drinking Water, Water Quality Section
P O Box 47822, Olympia, WA 98504-7822
| (360) 236-3132 |  | Email: | simon.tung@doh.wa.gov
Notes on Version 1.0 Revised 12/16/2005
Revisions in this version centers on the SWTR Monthly Disinfection Rept form:
Population served is now requested (Cell C8) so that minimum number of residual grab samples can be determined.
Purveyors may enter "C" in the column for number of chlorine residual samples collected if continuous residual monitoring is used (Column J).
Each "C" entry counts as 1 in number of samples collected.
Formatting for "Duration less than 0.2mg/L" has been modified to show up in bold red only if residual is less than 0.2mg/L.
Notes on Version 1.0 Revised 02/14/2006
Overall Log Treatment Required has been set to 3.0 on the SWTR Monthly Disinfection Rept form.
Entries in the Lowest Daily Residual in the SWTR Monthly Disinfection Rept has been adjusted to display one decimal place.
Notes on Version 1.0 Revised 03/17/2006
Slightly widened columns B & D on WTP Monthly Report sheet to accommodate larger total volumes of water treated and backwash.
Changed display of Total row (row 44) to suppress decimals.
Correction made on 3/24/2009 as per Mike Wilson re certain cells

## WTP Monthly Rept
[5 empty] | Water Treatment Plant Monthly Report Form | [13 empty] | Water Treatment Plant Monthly Report Form
[11 empty] | Month |  | Year | [11 empty] | Month | 0 | Year | 0
| PWS ID |  |  | PWS Name | [7 empty] | County |  |  |  |  | PWS ID | 0 |  | PWS Name |  | 0 |  |  |  |  | County | 0
| Source ID |  |  | Source Name | [7 empty] | Plant ID |  |  |  |  | Source ID | 0 |  | Source Name |  | 0 |  |  |  |  | Plant ID | 0
Cells and Columns with Blue Headings are intended for data provided by user
| Water Treated in 1000 gals | Total Hours of Operation | Filter Backwash Total in 1000 gal | Chemicals Used (lbs) | [7 empty] | Turbidity NTU |  | Combined Filter Effluent Turbidity 4 hour sample NTU | [6 empty] | No of Samples > 0.3 NTU | Max CFE Turbidity NTU | % NTU Reduction (See Note 1) | Temp C | pH |  | Total Alkalinity mg/L as CaCO3 |  | Calcium Hardness mg/L as CaCO3 Fin
Remarks
Date |  |  |  | Chlorine | Alum | Polymer | Filter Aid | Soda Ash | Ozone |  |  | Raw | Settled | 1st | 2nd | 3rd | 4th | 5th | 6th | Avg |  |  |  | Raw | Raw | Final | Raw | Fin
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 0
Avg
| Total number of CFE samples analyzed for month: N = | [5 empty] | 0 |  | Total number of CFE samples exceeding 0.3 NTU: E = |  |  |  |  | 3rd: 0
| Satisfactory turbidity performance is 95% or greater. Performance determination: [1-(E/N)]x100 = | [12 empty] | 4th: Report Submitted By | [5 empty] | Signature
| Number of times CFE exceeded 1.0 NTU this month: | [5 empty] | 0
| Did the CFE continuous monitoring fail to operate for more than five (5) consecutive days during this month? Y/N: | [12 empty] | 3rd: See Cover Page for information on where to send this form.
| DOH Form #331-023 (Excel version) | [12 empty] | 3rd: NOTE 1: Percent turbidity reduction for each day of operation: PTR = [(Raw NTU)-(Avg CFE NTU)]x(100)/(Raw NTU)

## SWTR Monthly Disinfection Rept
Washington State Department of Health
SWTR Disinfection Monthly Report Form
| PWS ID | 0 |  | PWS Name | 0 |  |  |  | Month | 0 | Year | 0
| County | 0 | [5 empty] | Submitted By
| Source ID | 0 |  | Source Name | 0 |  | . | WTPO Cert No
| Plant ID | 0 | [5 empty] | Telephone No
Population Served |  |  |  |  | Min Grab Samples Reqd | 1 | Residuals Normally Measured Continuously Y/N
Overall Log Treatment Req'd |  |  | 3 |  | Filtration Log Removal Credit |  |  |  |  | Required Disinfection Log Reduction |  |  |  | 3
Cells and Columns with Blue Headings are intended for data provided by user
|  |  | Inactivation Ratio Determination | [6 empty] | Disinfectant Residual at |  |  | Residual in
Note: For correct results, remember to enter your plant's Filtration Log Removal Credit in cell I9 above | [9 empty] | Distribution Entry Point |  |  | Distribution System
Date | Peak Hour Flow gpm | Water Temp C | pH | Chlorine Residual {C} mg/L | Contact Time {T} minutes | Calculated CT {C*T} | Required CT from Tables* | Inact Ratio {Calc CT/Req'd CT} | No. of Samples Collected "C" if Continuous | Lowest Daily Residual mg/L | Duration less than 0.2mg/L hours | DOH Notified? Name & Time | No of Sites Sampled | No of Samples Residual Not Detected
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
Total | [8 empty] | 0 | # < 0.2 mg/L | # > 4 hrs |  | 0 | 0
Count | [7 empty] | 0 |  | 0 | 0
Min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Max | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Avg
| *Adjusted for Log Reduction Required |  |  |  |  | No. Days Inact Ratio < 1 |  | 0
DOH Form #331-048 (Excel version) |  |  |  |  | See Cover Page for information on where to send this form. |  |  |  |  | Signature

## Monthly Summary
Surface Water Treatment Plant
Monthly Report Summary Form
PWS ID | 0 |  | Source ID | 0 |  |  | Month | 0 | Year | 0
PWS Name | 0 |  |  | Source Name |  | 0
|  |  |  | Plant ID | 0 |  |  | County | 0
|  | Color code for form information: | WTP Monthly Rept |  | SWTR Monthly Disinfection Rept |  |  | To be supplied by user
Source (Raw) Water | 7. Maximum density of raw water fecal coliform (# organisms/100 ml)
| 8. Number of days raw water turbidity was monitored this month | [7 empty] | 0
9. Average turbidity of the raw water treated by the plant (NTU)
| 10. Maximum turbidity of the raw water treated by the plant (NTU) | [7 empty] | 0
11. Number of raw water turbidity measurements taken
Filtration | 12. Hours of operation during reporting month | [7 empty] | 0
| 13. Number of filtered water turbidity measurements taken | [7 empty] | 0
| 14. Turbidity performance limit |  |  | No of filtered measurements > performance limit |  |  |  |  | 0
15. Average filtered water turbidity (NTU)
| 16. Maximum filtered water turbidity (NTU) | [7 empty] | 0
| 17. Average of daily filtration effectiveness calculations (% turbidity reduction) | [5 empty] | "X" if N/A:
| 18. Was unfiltered water provided to consumers at any time? | [6 empty] | Y/N:
| 19. Was coagulation in use at all times the plant was operating? | [6 empty] | Y/N/NA:
20. Maximum filtration rate (gpm/sq. ft)
Inactivation Ratio | 21. Number of days disinfectant CT was monitored this month | [7 empty] | 0
| 22. Number of days inactivation ratio was below 1.0 (Enter 0 if none) | [7 empty] | 0
| 23. Lowest inactivation ratio achieved | [7 empty] | 0
Distribution Entry Point Samples | 24. Number of days during which plant produced water during month | [7 empty] | 0
| 25. Number of entry point residual samples analyzed during month | [7 empty] | 0
| 26. No of days when residual fell below 0.2 mg/l (Enter 0 if none) | [7 empty] | 0
| 27. No of days when residual fell below 0.2 mg/l for more than 4 hours (Enter 0 if none) | [7 empty] | 0
Distribution System Residuals | 28. Number of days water served to public this month
29. Number of days distribution system disinfectant residual was monitored
| 30. No of distribution system disinfectant residual samples measured this month | [7 empty] | 0
| 31. No of samples where no disinfectant residual was detected (Enter 0 if none) | [7 empty] | 0
32. Average of all disinfectant residual measurements taken with coliform samples
Finished Water/ General | 33. Max allowable turbidity |  |  | No of finished water turbidity measurem't > limit |  |  |  |  | 0
| 34. Maximum flow rate treated (gpm) | [7 empty] | 0
35. Number of water quality complaints received from consumers served by system
| 36. Did certified operator take all req'd pH, temp, turbidity, and residual disinfectant conc? | [6 empty] | Y/N:
| 37. Were all turbidimeters calibrated w/ primary standard within last quarter? Date | [6 empty] | Y/N:
Report Submitted By | [5 empty] | BTO/WTPO Cert No
Signature | [5 empty] | Telephone Number
DOH Form #331-172 (Excel version) |  |  |  |  | See Cover Page for information on where to send this form.

## Req'd CT Calc (hidden)
| 0 | 501 | 1001 | 2501 | 3301 |  |  |  | 0 | 6 | 6.1 | 6.2 | 6.3 | 6.4 | 6.5 | 6.6 | 6.7 | 6.8 | 6.9 | 7 | 7.1 | 7.2 | 7.3 | 7.4 | 7.5 | 7.6 | 7.7 | 7.8 | 7.9 | 8 | 8.1 | 8.2 | 8.3 | 8.4 | 8.5 | 8.6 | 8.7 | 8.8 | 8.9 | 9
| 1 | 2 | 3 | 4 | 6 |  |  |  | 2 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32
| PopServed | 0 |  |  | MinGrab | 1
|  |  | Inactivation Ratio Determination | [5 empty] | 0 2: Disinfection Log Reduction Req'd; 6.3 5: 3
Date | Peak Hour Flow gpm | Water Temp C | pH | Chlorine Residual {C} mg/L | Contact Time {T} minutes | Calculated CT {C*T} | Required CT from Tables | Inact Ratio {Calc CT/Req'd CT} | 0 2: Temp Adj; 6 2: pH Offset; 6.1 3: Chlorine Adj; 6.2 4: CT; 6.3 5: CT Calc; 6.4 6: Table Lookup; 6.5 7: CT Required; 6.6 8: Inact Ratio; 6.8 10: Lowest Daily Residual mg/L; 6.9 11: Duration less than 0.2mg/L hours; 7 12: Valid Durations hours
1 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
2 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
3 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
4 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
5 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
6 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
7 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
8 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
9 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
10 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
11 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
12 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
13 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
14 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
15 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
16 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
17 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
18 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
19 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
20 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
21 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
22 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
23 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
24 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
25 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
26 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
27 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
28 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
29 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
30 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
31 | [8 empty] | 0 2: #VALUE!; 6 2: #VALUE!; 6.1 3: #VALUE!; 6.4 6: #VALUE!; 6.5 7: #VALUE!; 6.6 8: #VALUE!
Total
Count | [8 empty] | 7 12: 0
Min | [8 empty] | 6.8 10: 0; 6.9 11: 0; 7 12: 0
Max | [8 empty] | 6.8 10: 0; 6.9 11: 0; 7 12: 0
Avg
| ADAM | 3
| ASOT | 3
| BENT | 3
| CHEL | 3
| CLAL | 2
| CLAR | 2
| CLIC | 3
| COLO | 3
| COLU | 3
| COWL | 2
| DOUG | 3
| FERR | 3
| FRAN | 3
| GARF | 3
| GRAN | 3
| GRAY | 2
| ILAN | 1
| ISLA | 1
| JEFF | 2
| KING | 1
| KITI | 3
| KITS | 2
| KITT | 3
| KLIC | 3
| KOWL | 2
| LEWI | 2
| LINC | 3
| MASI | 2
| MASO | 2
| OKAN | 3
| OKON | 3
| PACI | 2
| PEIR | 1
| PEND | 3
| PIER | 1
| POND | 3
| SAN | 1
| SANJ | 1
| SKAG | 1
| SKAM | 2
| SNOH | 1
| SPOK | 3
| STEV | 3
| THUR | 2
| TURS | 2
| WALL | 3
| WATC | 1
| WHAT | 1
| WHIT | 3
| WITM | 3
| YAKA | 3
| YAKI | 3

## CT Lookup Table
Look-up Table for Required CT for 1 log Reduction in Giardia at Various Temperatures, Chlorine Concentration and pH
Temp | Chlorine | Lookup | [6 empty] | pH | [17 empty] | pH
Degrees | Conc | Row
C | (mg/l) |  | 6 | 6.1 | 6.2 | 6.3 | 6.4 | 6.5 | 6.6 | 6.7 | 6.8 | 6.9 | 7 | 7.1 | 7.2 | 7.3 | 7.4 | 7.5 | 7.6 | 7.7 | 7.8 | 7.9 | 8 | 8.1 | 8.2 | 8.3 | 8.4 | 8.5 | 8.6 | 8.7 | 8.8 | 8.9 | 9
0 | 0 | 0 | 46 | 47.6 | 49.2 | 50.8 | 52.4 | 54 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.8 | 70.6 | 73.4 | 76.2 | 79 | 81.6 | 84.2 | 86.8 | 89.4 | 92 | 95.6 | 99.2 | 102.8 | 106.4 | 110 | 114 | 118 | 122 | 126 | 130
0.5 | 0 | 500 | 46 | 47.6 | 49.2 | 50.8 | 52.4 | 54 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.8 | 70.6 | 73.4 | 76.2 | 79 | 81.6 | 84.2 | 86.8 | 89.4 | 92 | 95.6 | 99.2 | 102.8 | 106.4 | 110 | 114 | 118 | 122 | 126 | 130
0.5 | 0.4 | 504 | 46 | 47.6 | 49.2 | 50.8 | 52.4 | 54 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.8 | 70.6 | 73.4 | 76.2 | 79 | 81.6 | 84.2 | 86.8 | 89.4 | 92 | 95.6 | 99.2 | 102.8 | 106.4 | 110 | 114 | 118 | 122 | 126 | 130
0.5 | 0.6 | 506 | 47 | 48.8 | 50.6 | 52.4 | 54.2 | 56 | 58.2 | 60.4 | 62.6 | 64.8 | 67 | 69.6 | 72.2 | 74.8 | 77.4 | 80 | 83 | 86 | 89 | 92 | 95 | 98.8 | 102.6 | 106.4 | 110.2 | 114 | 118.4 | 122.8 | 127.2 | 131.6 | 136
0.5 | 0.8 | 508 | 48 | 49.8 | 51.6 | 53.4 | 55.2 | 57 | 59.2 | 61.4 | 63.6 | 65.8 | 68 | 70.8 | 73.6 | 76.4 | 79.2 | 82 | 85.2 | 88.4 | 91.6 | 94.8 | 98 | 102 | 106 | 110 | 114 | 118 | 122.6 | 127.2 | 131.8 | 136.4 | 141
0.5 | 1 | 510 | 49 | 51 | 53 | 55 | 57 | 59 | 61.2 | 63.4 | 65.6 | 67.8 | 70 | 72.8 | 75.6 | 78.4 | 81.2 | 84 | 87.4 | 90.8 | 94.2 | 97.6 | 101 | 105.2 | 109.4 | 113.6 | 117.8 | 122 | 126.8 | 131.6 | 136.4 | 141.2 | 146
0.5 | 1.2 | 512 | 51 | 52.8 | 54.6 | 56.4 | 58.2 | 60 | 62.4 | 64.8 | 67.2 | 69.6 | 72 | 74.8 | 77.6 | 80.4 | 83.2 | 86 | 89.6 | 93.2 | 96.8 | 100.4 | 104 | 108.2 | 112.4 | 116.6 | 120.8 | 125 | 130 | 135 | 140 | 145 | 150
0.5 | 1.4 | 514 | 52 | 53.8 | 55.6 | 57.4 | 59.2 | 61 | 63.6 | 66.2 | 68.8 | 71.4 | 74 | 77 | 80 | 83 | 86 | 89 | 92.6 | 96.2 | 99.8 | 103.4 | 107 | 111.4 | 115.8 | 120.2 | 124.6 | 129 | 134.2 | 139.4 | 144.6 | 149.8 | 155
0.5 | 1.6 | 516 | 52 | 54.2 | 56.4 | 58.6 | 60.8 | 63 | 65.4 | 67.8 | 70.2 | 72.6 | 75 | 78.2 | 81.4 | 84.6 | 87.8 | 91 | 94.8 | 98.6 | 102.4 | 106.2 | 110 | 114.4 | 118.8 | 123.2 | 127.6 | 132 | 137.4 | 142.8 | 148.2 | 153.6 | 159
0.5 | 1.8 | 518 | 54 | 56 | 58 | 60 | 62 | 64 | 66.6 | 69.2 | 71.8 | 74.4 | 77 | 80.2 | 83.4 | 86.6 | 89.8 | 93 | 97 | 101 | 105 | 109 | 113 | 117.6 | 122.2 | 126.8 | 131.4 | 136 | 141.4 | 146.8 | 152.2 | 157.6 | 163
0.5 | 2 | 520 | 55 | 57.2 | 59.4 | 61.6 | 63.8 | 66 | 68.6 | 71.2 | 73.8 | 76.4 | 79 | 82.2 | 85.4 | 88.6 | 91.8 | 95 | 99 | 103 | 107 | 111 | 115 | 119.8 | 124.6 | 129.4 | 134.2 | 139 | 144.6 | 150.2 | 155.8 | 161.4 | 167
0.5 | 2.2 | 522 | 56 | 58.2 | 60.4 | 62.6 | 64.8 | 67 | 69.8 | 72.6 | 75.4 | 78.2 | 81 | 84.6 | 88.2 | 91.8 | 95.4 | 99 | 102.8 | 106.6 | 110.4 | 114.2 | 118 | 122.8 | 127.6 | 132.4 | 137.2 | 142 | 147.6 | 153.2 | 158.8 | 164.4 | 170
0.5 | 2.4 | 524 | 57 | 59.2 | 61.4 | 63.6 | 65.8 | 68 | 70.8 | 73.6 | 76.4 | 79.2 | 82 | 85.4 | 88.8 | 92.2 | 95.6 | 99 | 103.2 | 107.4 | 111.6 | 115.8 | 120 | 125 | 130 | 135 | 140 | 145 | 150.8 | 156.6 | 162.4 | 168.2 | 174
0.5 | 2.6 | 526 | 58 | 60.4 | 62.8 | 65.2 | 67.6 | 70 | 72.8 | 75.6 | 78.4 | 81.2 | 84 | 87.4 | 90.8 | 94.2 | 97.6 | 101 | 105.4 | 109.8 | 114.2 | 118.6 | 123 | 128 | 133 | 138 | 143 | 148 | 154 | 160 | 166 | 172 | 178
0.5 | 2.8 | 528 | 59 | 61.4 | 63.8 | 66.2 | 68.6 | 71 | 74 | 77 | 80 | 83 | 86 | 89.4 | 92.8 | 96.2 | 99.6 | 103 | 107.4 | 111.8 | 116.2 | 120.6 | 125 | 130.2 | 135.4 | 140.6 | 145.8 | 151 | 157 | 163 | 169 | 175 | 181
0.5 | 3 | 530 | 60 | 62.4 | 64.8 | 67.2 | 69.6 | 72 | 75 | 78 | 81 | 84 | 87 | 90.6 | 94.2 | 97.8 | 101.4 | 105 | 109.4 | 113.8 | 118.2 | 122.6 | 127 | 132.2 | 137.4 | 142.6 | 147.8 | 153 | 159.2 | 165.4 | 171.6 | 177.8 | 184
1 | 0 | 1000 | 44.4444 | 46.0222 | 47.6 | 49.1778 | 50.7556 | 52.3333 | 54.4444 | 56.5556 | 58.6667 | 60.7778 | 62.8889 | 65.5778 | 68.2667 | 70.9556 | 73.6444 | 76.3333 | 78.8889 | 81.4444 | 84 | 86.5556 | 89.1111 | 92.6 | 96.0889 | 99.5778 | 103.0667 | 106.5556 | 110.4222 | 114.2889 | 118.1556 | 122.0222 | 125.8889
1 | 0.4 | 1004 | 44.4444 | 46.0222 | 47.6 | 49.1778 | 50.7556 | 52.3333 | 54.4444 | 56.5556 | 58.6667 | 60.7778 | 62.8889 | 65.5778 | 68.2667 | 70.9556 | 73.6444 | 76.3333 | 78.8889 | 81.4444 | 84 | 86.5556 | 89.1111 | 92.6 | 96.0889 | 99.5778 | 103.0667 | 106.5556 | 110.4222 | 114.2889 | 118.1556 | 122.0222 | 125.8889
1 | 0.6 | 1006 | 45.4444 | 47.2 | 48.9556 | 50.7111 | 52.4667 | 54.2222 | 56.3556 | 58.4889 | 60.6222 | 62.7556 | 64.8889 | 67.4 | 69.9111 | 72.4222 | 74.9333 | 77.4444 | 80.3556 | 83.2667 | 86.1778 | 89.0889 | 92 | 95.6667 | 99.3333 | 103 | 106.6667 | 110.3333 | 114.6 | 118.8667 | 123.1333 | 127.4 | 131.6667
1 | 0.8 | 1008 | 46.4444 | 48.2 | 49.9556 | 51.7111 | 53.4667 | 55.2222 | 57.3556 | 59.4889 | 61.6222 | 63.7556 | 65.8889 | 68.5778 | 71.2667 | 73.9556 | 76.6444 | 79.3333 | 82.4444 | 85.5556 | 88.6667 | 91.7778 | 94.8889 | 98.7556 | 102.6222 | 106.4889 | 110.3556 | 114.2222 | 118.6667 | 123.1111 | 127.5556 | 132 | 136.4444
1 | 1 | 1010 | 47.4444 | 49.3778 | 51.3111 | 53.2444 | 55.1778 | 57.1111 | 59.2444 | 61.3778 | 63.5111 | 65.6444 | 67.7778 | 70.4889 | 73.2 | 75.9111 | 78.6222 | 81.3333 | 84.6222 | 87.9111 | 91.2 | 94.4889 | 97.7778 | 101.8444 | 105.9111 | 109.9778 | 114.0444 | 118.1111 | 122.7556 | 127.4 | 132.0444 | 136.6889 | 141.3333
1 | 1.2 | 1012 | 49.3333 | 51.0667 | 52.8 | 54.5333 | 56.2667 | 58 | 60.3333 | 62.6667 | 65 | 67.3333 | 69.6667 | 72.3778 | 75.0889 | 77.8 | 80.5111 | 83.2222 | 86.7111 | 90.2 | 93.6889 | 97.1778 | 100.6667 | 104.7333 | 108.8 | 112.8667 | 116.9333 | 121 | 125.8444 | 130.6889 | 135.5333 | 140.3778 | 145.2222
1 | 1.4 | 1014 | 50.2222 | 51.9778 | 53.7333 | 55.4889 | 57.2444 | 59 | 61.5111 | 64.0222 | 66.5333 | 69.0444 | 71.5556 | 74.4444 | 77.3333 | 80.2222 | 83.1111 | 86 | 89.5111 | 93.0222 | 96.5333 | 100.0444 | 103.5556 | 107.8 | 112.0444 | 116.2889 | 120.5333 | 124.7778 | 129.8222 | 134.8667 | 139.9111 | 144.9556 | 150
1 | 1.6 | 1016 | 50.3333 | 52.4444 | 54.5556 | 56.6667 | 58.7778 | 60.8889 | 63.2222 | 65.5556 | 67.8889 | 70.2222 | 72.5556 | 75.6444 | 78.7333 | 81.8222 | 84.9111 | 88 | 91.6667 | 95.3333 | 99 | 102.6667 | 106.3333 | 110.6222 | 114.9111 | 119.2 | 123.4889 | 127.7778 | 132.9778 | 138.1778 | 143.3778 | 148.5778 | 153.7778
1 | 1.8 | 1018 | 52.2222 | 54.1556 | 56.0889 | 58.0222 | 59.9556 | 61.8889 | 64.4 | 66.9111 | 69.4222 | 71.9333 | 74.4444 | 77.5333 | 80.6222 | 83.7111 | 86.8 | 89.8889 | 93.7556 | 97.6222 | 101.4889 | 105.3556 | 109.2222 | 113.6889 | 118.1556 | 122.6222 | 127.0889 | 131.5556 | 136.7778 | 142 | 147.2222 | 152.4444 | 157.6667
1 | 2 | 1020 | 53.2222 | 55.3333 | 57.4444 | 59.5556 | 61.6667 | 63.7778 | 66.2889 | 68.8 | 71.3111 | 73.8222 | 76.3333 | 79.4444 | 82.5556 | 85.6667 | 88.7778 | 91.8889 | 95.7556 | 99.6222 | 103.4889 | 107.3556 | 111.2222 | 115.8667 | 120.5111 | 125.1556 | 129.8 | 134.4444 | 139.8667 | 145.2889 | 150.7111 | 156.1333 | 161.5556
1 | 2.2 | 1022 | 54.1111 | 56.2444 | 58.3778 | 60.5111 | 62.6444 | 64.7778 | 67.4667 | 70.1556 | 72.8444 | 75.5333 | 78.2222 | 81.6889 | 85.1556 | 88.6222 | 92.0889 | 95.5556 | 99.2667 | 102.9778 | 106.6889 | 110.4 | 114.1111 | 118.7556 | 123.4 | 128.0444 | 132.6889 | 137.3333 | 142.7556 | 148.1778 | 153.6 | 159.0222 | 164.4444
1 | 2.4 | 1024 | 55.1111 | 57.2444 | 59.3778 | 61.5111 | 63.6444 | 65.7778 | 68.4667 | 71.1556 | 73.8444 | 76.5333 | 79.2222 | 82.5333 | 85.8444 | 89.1556 | 92.4667 | 95.7778 | 99.8222 | 103.8667 | 107.9111 | 111.9556 | 116 | 120.8444 | 125.6889 | 130.5333 | 135.3778 | 140.2222 | 145.8444 | 151.4667 | 157.0889 | 162.7111 | 168.3333
1 | 2.6 | 1026 | 56.1111 | 58.4222 | 60.7333 | 63.0444 | 65.3556 | 67.6667 | 70.3556 | 73.0444 | 75.7333 | 78.4222 | 81.1111 | 84.4222 | 87.7333 | 91.0444 | 94.3556 | 97.6667 | 101.9111 | 106.1556 | 110.4 | 114.6444 | 118.8889 | 123.7333 | 128.5778 | 133.4222 | 138.2667 | 143.1111 | 148.9111 | 154.7111 | 160.5111 | 166.3111 | 172.1111
1 | 2.8 | 1028 | 57 | 59.3111 | 61.6222 | 63.9333 | 66.2444 | 68.5556 | 71.4444 | 74.3333 | 77.2222 | 80.1111 | 83 | 86.3111 | 89.6222 | 92.9333 | 96.2444 | 99.5556 | 103.8222 | 108.0889 | 112.3556 | 116.6222 | 120.8889 | 125.9111 | 130.9333 | 135.9556 | 140.9778 | 146 | 151.8 | 157.6 | 163.4 | 169.2 | 175
1 | 3 | 1030 | 58 | 60.3111 | 62.6222 | 64.9333 | 67.2444 | 69.5556 | 72.4667 | 75.3778 | 78.2889 | 81.2 | 84.1111 | 87.6 | 91.0889 | 94.5778 | 98.0667 | 101.5556 | 105.8 | 110.0444 | 114.2889 | 118.5333 | 122.7778 | 127.8222 | 132.8667 | 137.9111 | 142.9556 | 148 | 154 | 160 | 166 | 172 | 178
2 | 0 | 2000 | 41.3333 | 42.8667 | 44.4 | 45.9333 | 47.4667 | 49 | 50.9333 | 52.8667 | 54.8 | 56.7333 | 58.6667 | 61.1333 | 63.6 | 66.0667 | 68.5333 | 71 | 73.4667 | 75.9333 | 78.4 | 80.8667 | 83.3333 | 86.6 | 89.8667 | 93.1333 | 96.4 | 99.6667 | 103.2667 | 106.8667 | 110.4667 | 114.0667 | 117.6667
2 | 0.4 | 2004 | 41.3333 | 42.8667 | 44.4 | 45.9333 | 47.4667 | 49 | 50.9333 | 52.8667 | 54.8 | 56.7333 | 58.6667 | 61.1333 | 63.6 | 66.0667 | 68.5333 | 71 | 73.4667 | 75.9333 | 78.4 | 80.8667 | 83.3333 | 86.6 | 89.8667 | 93.1333 | 96.4 | 99.6667 | 103.2667 | 106.8667 | 110.4667 | 114.0667 | 117.6667
2 | 0.6 | 2006 | 42.3333 | 44 | 45.6667 | 47.3333 | 49 | 50.6667 | 52.6667 | 54.6667 | 56.6667 | 58.6667 | 60.6667 | 63 | 65.3333 | 67.6667 | 70 | 72.3333 | 75.0667 | 77.8 | 80.5333 | 83.2667 | 86 | 89.4 | 92.8 | 96.2 | 99.6 | 103 | 107 | 111 | 115 | 119 | 123
2 | 0.8 | 2008 | 43.3333 | 45 | 46.6667 | 48.3333 | 50 | 51.6667 | 53.6667 | 55.6667 | 57.6667 | 59.6667 | 61.6667 | 64.1333 | 66.6 | 69.0667 | 71.5333 | 74 | 76.9333 | 79.8667 | 82.8 | 85.7333 | 88.6667 | 92.2667 | 95.8667 | 99.4667 | 103.0667 | 106.6667 | 110.8 | 114.9333 | 119.0667 | 123.2 | 127.3333
2 | 1 | 2010 | 44.3333 | 46.1333 | 47.9333 | 49.7333 | 51.5333 | 53.3333 | 55.3333 | 57.3333 | 59.3333 | 61.3333 | 63.3333 | 65.8667 | 68.4 | 70.9333 | 73.4667 | 76 | 79.0667 | 82.1333 | 85.2 | 88.2667 | 91.3333 | 95.1333 | 98.9333 | 102.7333 | 106.5333 | 110.3333 | 114.6667 | 119 | 123.3333 | 127.6667 | 132
2 | 1.2 | 2012 | 46 | 47.6 | 49.2 | 50.8 | 52.4 | 54 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.5333 | 70.0667 | 72.6 | 75.1333 | 77.6667 | 80.9333 | 84.2 | 87.4667 | 90.7333 | 94 | 97.8 | 101.6 | 105.4 | 109.2 | 113 | 117.5333 | 122.0667 | 126.6 | 131.1333 | 135.6667
2 | 1.4 | 2014 | 46.6667 | 48.3333 | 50 | 51.6667 | 53.3333 | 55 | 57.3333 | 59.6667 | 62 | 64.3333 | 66.6667 | 69.3333 | 72 | 74.6667 | 77.3333 | 80 | 83.3333 | 86.6667 | 90 | 93.3333 | 96.6667 | 100.6 | 104.5333 | 108.4667 | 112.4 | 116.3333 | 121.0667 | 125.8 | 130.5333 | 135.2667 | 140
2 | 1.6 | 2016 | 47 | 48.9333 | 50.8667 | 52.8 | 54.7333 | 56.6667 | 58.8667 | 61.0667 | 63.2667 | 65.4667 | 67.6667 | 70.5333 | 73.4 | 76.2667 | 79.1333 | 82 | 85.4 | 88.8 | 92.2 | 95.6 | 99 | 103.0667 | 107.1333 | 111.2 | 115.2667 | 119.3333 | 124.1333 | 128.9333 | 133.7333 | 138.5333 | 143.3333
2 | 1.8 | 2018 | 48.6667 | 50.4667 | 52.2667 | 54.0667 | 55.8667 | 57.6667 | 60 | 62.3333 | 64.6667 | 67 | 69.3333 | 72.2 | 75.0667 | 77.9333 | 80.8 | 83.6667 | 87.2667 | 90.8667 | 94.4667 | 98.0667 | 101.6667 | 105.8667 | 110.0667 | 114.2667 | 118.4667 | 122.6667 | 127.5333 | 132.4 | 137.2667 | 142.1333 | 147
2 | 2 | 2020 | 49.6667 | 51.6 | 53.5333 | 55.4667 | 57.4 | 59.3333 | 61.6667 | 64 | 66.3333 | 68.6667 | 71 | 73.9333 | 76.8667 | 79.8 | 82.7333 | 85.6667 | 89.2667 | 92.8667 | 96.4667 | 100.0667 | 103.6667 | 108 | 112.3333 | 116.6667 | 121 | 125.3333 | 130.4 | 135.4667 | 140.5333 | 145.6 | 150.6667
2 | 2.2 | 2022 | 50.3333 | 52.3333 | 54.3333 | 56.3333 | 58.3333 | 60.3333 | 62.8 | 65.2667 | 67.7333 | 70.2 | 72.6667 | 75.8667 | 79.0667 | 82.2667 | 85.4667 | 88.6667 | 92.2 | 95.7333 | 99.2667 | 102.8 | 106.3333 | 110.6667 | 115 | 119.3333 | 123.6667 | 128 | 133.0667 | 138.1333 | 143.2 | 148.2667 | 153.3333
2 | 2.4 | 2024 | 51.3333 | 53.3333 | 55.3333 | 57.3333 | 59.3333 | 61.3333 | 63.8 | 66.2667 | 68.7333 | 71.2 | 73.6667 | 76.8 | 79.9333 | 83.0667 | 86.2 | 89.3333 | 93.0667 | 96.8 | 100.5333 | 104.2667 | 108 | 112.5333 | 117.0667 | 121.6 | 126.1333 | 130.6667 | 135.9333 | 141.2 | 146.4667 | 151.7333 | 157
2 | 2.6 | 2026 | 52.3333 | 54.4667 | 56.6 | 58.7333 | 60.8667 | 63 | 65.4667 | 67.9333 | 70.4 | 72.8667 | 75.3333 | 78.4667 | 81.6 | 84.7333 | 87.8667 | 91 | 94.9333 | 98.8667 | 102.8 | 106.7333 | 110.6667 | 115.2 | 119.7333 | 124.2667 | 128.8 | 133.3333 | 138.7333 | 144.1333 | 149.5333 | 154.9333 | 160.3333
2 | 2.8 | 2028 | 53 | 55.1333 | 57.2667 | 59.4 | 61.5333 | 63.6667 | 66.3333 | 69 | 71.6667 | 74.3333 | 77 | 80.1333 | 83.2667 | 86.4 | 89.5333 | 92.6667 | 96.6667 | 100.6667 | 104.6667 | 108.6667 | 112.6667 | 117.3333 | 122 | 126.6667 | 131.3333 | 136 | 141.4 | 146.8 | 152.2 | 157.6 | 163
2 | 3 | 2030 | 54 | 56.1333 | 58.2667 | 60.4 | 62.5333 | 64.6667 | 67.4 | 70.1333 | 72.8667 | 75.6 | 78.3333 | 81.6 | 84.8667 | 88.1333 | 91.4 | 94.6667 | 98.6 | 102.5333 | 106.4667 | 110.4 | 114.3333 | 119.0667 | 123.8 | 128.5333 | 133.2667 | 138 | 143.6 | 149.2 | 154.8 | 160.4 | 166
3 | 0 | 3000 | 38.2222 | 39.7111 | 41.2 | 42.6889 | 44.1778 | 45.6667 | 47.4222 | 49.1778 | 50.9333 | 52.6889 | 54.4444 | 56.6889 | 58.9333 | 61.1778 | 63.4222 | 65.6667 | 68.0444 | 70.4222 | 72.8 | 75.1778 | 77.5556 | 80.6 | 83.6444 | 86.6889 | 89.7333 | 92.7778 | 96.1111 | 99.4444 | 102.7778 | 106.1111 | 109.4444
3 | 0.4 | 3004 | 38.2222 | 39.7111 | 41.2 | 42.6889 | 44.1778 | 45.6667 | 47.4222 | 49.1778 | 50.9333 | 52.6889 | 54.4444 | 56.6889 | 58.9333 | 61.1778 | 63.4222 | 65.6667 | 68.0444 | 70.4222 | 72.8 | 75.1778 | 77.5556 | 80.6 | 83.6444 | 86.6889 | 89.7333 | 92.7778 | 96.1111 | 99.4444 | 102.7778 | 106.1111 | 109.4444
3 | 0.6 | 3006 | 39.2222 | 40.8 | 42.3778 | 43.9556 | 45.5333 | 47.1111 | 48.9778 | 50.8444 | 52.7111 | 54.5778 | 56.4444 | 58.6 | 60.7556 | 62.9111 | 65.0667 | 67.2222 | 69.7778 | 72.3333 | 74.8889 | 77.4444 | 80 | 83.1333 | 86.2667 | 89.4 | 92.5333 | 95.6667 | 99.4 | 103.1333 | 106.8667 | 110.6 | 114.3333
3 | 0.8 | 3008 | 40.2222 | 41.8 | 43.3778 | 44.9556 | 46.5333 | 48.1111 | 49.9778 | 51.8444 | 53.7111 | 55.5778 | 57.4444 | 59.6889 | 61.9333 | 64.1778 | 66.4222 | 68.6667 | 71.4222 | 74.1778 | 76.9333 | 79.6889 | 82.4444 | 85.7778 | 89.1111 | 92.4444 | 95.7778 | 99.1111 | 102.9333 | 106.7556 | 110.5778 | 114.4 | 118.2222
3 | 1 | 3010 | 41.2222 | 42.8889 | 44.5556 | 46.2222 | 47.8889 | 49.5556 | 51.4222 | 53.2889 | 55.1556 | 57.0222 | 58.8889 | 61.2444 | 63.6 | 65.9556 | 68.3111 | 70.6667 | 73.5111 | 76.3556 | 79.2 | 82.0444 | 84.8889 | 88.4222 | 91.9556 | 95.4889 | 99.0222 | 102.5556 | 106.5778 | 110.6 | 114.6222 | 118.6444 | 122.6667
3 | 1.2 | 3012 | 42.6667 | 44.1333 | 45.6 | 47.0667 | 48.5333 | 50 | 52.0667 | 54.1333 | 56.2 | 58.2667 | 60.3333 | 62.6889 | 65.0444 | 67.4 | 69.7556 | 72.1111 | 75.1556 | 78.2 | 81.2444 | 84.2889 | 87.3333 | 90.8667 | 94.4 | 97.9333 | 101.4667 | 105 | 109.2222 | 113.4444 | 117.6667 | 121.8889 | 126.1111
3 | 1.4 | 3014 | 43.1111 | 44.6889 | 46.2667 | 47.8444 | 49.4222 | 51 | 53.1556 | 55.3111 | 57.4667 | 59.6222 | 61.7778 | 64.2222 | 66.6667 | 69.1111 | 71.5556 | 74 | 77.1556 | 80.3111 | 83.4667 | 86.6222 | 89.7778 | 93.4 | 97.0222 | 100.6444 | 104.2667 | 107.8889 | 112.3111 | 116.7333 | 121.1556 | 125.5778 | 130
3 | 1.6 | 3016 | 43.6667 | 45.4222 | 47.1778 | 48.9333 | 50.6889 | 52.4444 | 54.5111 | 56.5778 | 58.6444 | 60.7111 | 62.7778 | 65.4222 | 68.0667 | 70.7111 | 73.3556 | 76 | 79.1333 | 82.2667 | 85.4 | 88.5333 | 91.6667 | 95.5111 | 99.3556 | 103.2 | 107.0444 | 110.8889 | 115.2889 | 119.6889 | 124.0889 | 128.4889 | 132.8889
3 | 1.8 | 3018 | 45.1111 | 46.7778 | 48.4444 | 50.1111 | 51.7778 | 53.4444 | 55.6 | 57.7556 | 59.9111 | 62.0667 | 64.2222 | 66.8667 | 69.5111 | 72.1556 | 74.8 | 77.4444 | 80.7778 | 84.1111 | 87.4444 | 90.7778 | 94.1111 | 98.0444 | 101.9778 | 105.9111 | 109.8444 | 113.7778 | 118.2889 | 122.8 | 127.3111 | 131.8222 | 136.3333
3 | 2 | 3020 | 46.1111 | 47.8667 | 49.6222 | 51.3778 | 53.1333 | 54.8889 | 57.0444 | 59.2 | 61.3556 | 63.5111 | 65.6667 | 68.4222 | 71.1778 | 73.9333 | 76.6889 | 79.4444 | 82.7778 | 86.1111 | 89.4444 | 92.7778 | 96.1111 | 100.1333 | 104.1556 | 108.1778 | 112.2 | 116.2222 | 120.9333 | 125.6444 | 130.3556 | 135.0667 | 139.7778
3 | 2.2 | 3022 | 46.5556 | 48.4222 | 50.2889 | 52.1556 | 54.0222 | 55.8889 | 58.1333 | 60.3778 | 62.6222 | 64.8667 | 67.1111 | 70.0444 | 72.9778 | 75.9111 | 78.8444 | 81.7778 | 85.1333 | 88.4889 | 91.8444 | 95.2 | 98.5556 | 102.5778 | 106.6 | 110.6222 | 114.6444 | 118.6667 | 123.3778 | 128.0889 | 132.8 | 137.5111 | 142.2222
3 | 2.4 | 3024 | 47.5556 | 49.4222 | 51.2889 | 53.1556 | 55.0222 | 56.8889 | 59.1333 | 61.3778 | 63.6222 | 65.8667 | 68.1111 | 71.0667 | 74.0222 | 76.9778 | 79.9333 | 82.8889 | 86.3111 | 89.7333 | 93.1556 | 96.5778 | 100 | 104.2222 | 108.4444 | 112.6667 | 116.8889 | 121.1111 | 126.0222 | 130.9333 | 135.8444 | 140.7556 | 145.6667
3 | 2.6 | 3026 | 48.5556 | 50.5111 | 52.4667 | 54.4222 | 56.3778 | 58.3333 | 60.5778 | 62.8222 | 65.0667 | 67.3111 | 69.5556 | 72.5111 | 75.4667 | 78.4222 | 81.3778 | 84.3333 | 87.9556 | 91.5778 | 95.2 | 98.8222 | 102.4444 | 106.6667 | 110.8889 | 115.1111 | 119.3333 | 123.5556 | 128.5556 | 133.5556 | 138.5556 | 143.5556 | 148.5556
3 | 2.8 | 3028 | 49 | 50.9556 | 52.9111 | 54.8667 | 56.8222 | 58.7778 | 61.2222 | 63.6667 | 66.1111 | 68.5556 | 71 | 73.9556 | 76.9111 | 79.8667 | 82.8222 | 85.7778 | 89.5111 | 93.2444 | 96.9778 | 100.7111 | 104.4444 | 108.7556 | 113.0667 | 117.3778 | 121.6889 | 126 | 131 | 136 | 141 | 146 | 151
3 | 3 | 3030 | 50 | 51.9556 | 53.9111 | 55.8667 | 57.8222 | 59.7778 | 62.3333 | 64.8889 | 67.4444 | 70 | 72.5556 | 75.6 | 78.6444 | 81.6889 | 84.7333 | 87.7778 | 91.4 | 95.0222 | 98.6444 | 102.2667 | 105.8889 | 110.3111 | 114.7333 | 119.1556 | 123.5778 | 128 | 133.2 | 138.4 | 143.6 | 148.8 | 154
4 | 0 | 4000 | 35.1111 | 36.5556 | 38 | 39.4444 | 40.8889 | 42.3333 | 43.9111 | 45.4889 | 47.0667 | 48.6444 | 50.2222 | 52.2444 | 54.2667 | 56.2889 | 58.3111 | 60.3333 | 62.6222 | 64.9111 | 67.2 | 69.4889 | 71.7778 | 74.6 | 77.4222 | 80.2444 | 83.0667 | 85.8889 | 88.9556 | 92.0222 | 95.0889 | 98.1556 | 101.2222
4 | 0.4 | 4004 | 35.1111 | 36.5556 | 38 | 39.4444 | 40.8889 | 42.3333 | 43.9111 | 45.4889 | 47.0667 | 48.6444 | 50.2222 | 52.2444 | 54.2667 | 56.2889 | 58.3111 | 60.3333 | 62.6222 | 64.9111 | 67.2 | 69.4889 | 71.7778 | 74.6 | 77.4222 | 80.2444 | 83.0667 | 85.8889 | 88.9556 | 92.0222 | 95.0889 | 98.1556 | 101.2222
4 | 0.6 | 4006 | 36.1111 | 37.6 | 39.0889 | 40.5778 | 42.0667 | 43.5556 | 45.2889 | 47.0222 | 48.7556 | 50.4889 | 52.2222 | 54.2 | 56.1778 | 58.1556 | 60.1333 | 62.1111 | 64.4889 | 66.8667 | 69.2444 | 71.6222 | 74 | 76.8667 | 79.7333 | 82.6 | 85.4667 | 88.3333 | 91.8 | 95.2667 | 98.7333 | 102.2 | 105.6667
4 | 0.8 | 4008 | 37.1111 | 38.6 | 40.0889 | 41.5778 | 43.0667 | 44.5556 | 46.2889 | 48.0222 | 49.7556 | 51.4889 | 53.2222 | 55.2444 | 57.2667 | 59.2889 | 61.3111 | 63.3333 | 65.9111 | 68.4889 | 71.0667 | 73.6444 | 76.2222 | 79.2889 | 82.3556 | 85.4222 | 88.4889 | 91.5556 | 95.0667 | 98.5778 | 102.0889 | 105.6 | 109.1111
4 | 1 | 4010 | 38.1111 | 39.6444 | 41.1778 | 42.7111 | 44.2444 | 45.7778 | 47.5111 | 49.2444 | 50.9778 | 52.7111 | 54.4444 | 56.6222 | 58.8 | 60.9778 | 63.1556 | 65.3333 | 67.9556 | 70.5778 | 73.2 | 75.8222 | 78.4444 | 81.7111 | 84.9778 | 88.2444 | 91.5111 | 94.7778 | 98.4889 | 102.2 | 105.9111 | 109.6222 | 113.3333
4 | 1.2 | 4012 | 39.3333 | 40.6667 | 42 | 43.3333 | 44.6667 | 46 | 47.9333 | 49.8667 | 51.8 | 53.7333 | 55.6667 | 57.8444 | 60.0222 | 62.2 | 64.3778 | 66.5556 | 69.3778 | 72.2 | 75.0222 | 77.8444 | 80.6667 | 83.9333 | 87.2 | 90.4667 | 93.7333 | 97 | 100.9111 | 104.8222 | 108.7333 | 112.6444 | 116.5556
4 | 1.4 | 4014 | 39.5556 | 41.0444 | 42.5333 | 44.0222 | 45.5111 | 47 | 48.9778 | 50.9556 | 52.9333 | 54.9111 | 56.8889 | 59.1111 | 61.3333 | 63.5556 | 65.7778 | 68 | 70.9778 | 73.9556 | 76.9333 | 79.9111 | 82.8889 | 86.2 | 89.5111 | 92.8222 | 96.1333 | 99.4444 | 103.5556 | 107.6667 | 111.7778 | 115.8889 | 120
4 | 1.6 | 4016 | 40.3333 | 41.9111 | 43.4889 | 45.0667 | 46.6444 | 48.2222 | 50.1556 | 52.0889 | 54.0222 | 55.9556 | 57.8889 | 60.3111 | 62.7333 | 65.1556 | 67.5778 | 70 | 72.8667 | 75.7333 | 78.6 | 81.4667 | 84.3333 | 87.9556 | 91.5778 | 95.2 | 98.8222 | 102.4444 | 106.4444 | 110.4444 | 114.4444 | 118.4444 | 122.4444
4 | 1.8 | 4018 | 41.5556 | 43.0889 | 44.6222 | 46.1556 | 47.6889 | 49.2222 | 51.2 | 53.1778 | 55.1556 | 57.1333 | 59.1111 | 61.5333 | 63.9556 | 66.3778 | 68.8 | 71.2222 | 74.2889 | 77.3556 | 80.4222 | 83.4889 | 86.5556 | 90.2222 | 93.8889 | 97.5556 | 101.2222 | 104.8889 | 109.0444 | 113.2 | 117.3556 | 121.5111 | 125.6667
4 | 2 | 4020 | 42.5556 | 44.1333 | 45.7111 | 47.2889 | 48.8667 | 50.4444 | 52.4222 | 54.4 | 56.3778 | 58.3556 | 60.3333 | 62.9111 | 65.4889 | 68.0667 | 70.6444 | 73.2222 | 76.2889 | 79.3556 | 82.4222 | 85.4889 | 88.5556 | 92.2667 | 95.9778 | 99.6889 | 103.4 | 107.1111 | 111.4667 | 115.8222 | 120.1778 | 124.5333 | 128.8889
4 | 2.2 | 4022 | 42.7778 | 44.5111 | 46.2444 | 47.9778 | 49.7111 | 51.4444 | 53.4667 | 55.4889 | 57.5111 | 59.5333 | 61.5556 | 64.2222 | 66.8889 | 69.5556 | 72.2222 | 74.8889 | 78.0667 | 81.2444 | 84.4222 | 87.6 | 90.7778 | 94.4889 | 98.2 | 101.9111 | 105.6222 | 109.3333 | 113.6889 | 118.0444 | 122.4 | 126.7556 | 131.1111
4 | 2.4 | 4024 | 43.7778 | 45.5111 | 47.2444 | 48.9778 | 50.7111 | 52.4444 | 54.4667 | 56.4889 | 58.5111 | 60.5333 | 62.5556 | 65.3333 | 68.1111 | 70.8889 | 73.6667 | 76.4444 | 79.5556 | 82.6667 | 85.7778 | 88.8889 | 92 | 95.9111 | 99.8222 | 103.7333 | 107.6444 | 111.5556 | 116.1111 | 120.6667 | 125.2222 | 129.7778 | 134.3333
4 | 2.6 | 4026 | 44.7778 | 46.5556 | 48.3333 | 50.1111 | 51.8889 | 53.6667 | 55.6889 | 57.7111 | 59.7333 | 61.7556 | 63.7778 | 66.5556 | 69.3333 | 72.1111 | 74.8889 | 77.6667 | 80.9778 | 84.2889 | 87.6 | 90.9111 | 94.2222 | 98.1333 | 102.0444 | 105.9556 | 109.8667 | 113.7778 | 118.3778 | 122.9778 | 127.5778 | 132.1778 | 136.7778
4 | 2.8 | 4028 | 45 | 46.7778 | 48.5556 | 50.3333 | 52.1111 | 53.8889 | 56.1111 | 58.3333 | 60.5556 | 62.7778 | 65 | 67.7778 | 70.5556 | 73.3333 | 76.1111 | 78.8889 | 82.3556 | 85.8222 | 89.2889 | 92.7556 | 96.2222 | 100.1778 | 104.1333 | 108.0889 | 112.0444 | 116 | 120.6 | 125.2 | 129.8 | 134.4 | 139
4 | 3 | 4030 | 46 | 47.7778 | 49.5556 | 51.3333 | 53.1111 | 54.8889 | 57.2667 | 59.6444 | 62.0222 | 64.4 | 66.7778 | 69.6 | 72.4222 | 75.2444 | 78.0667 | 80.8889 | 84.2 | 87.5111 | 90.8222 | 94.1333 | 97.4444 | 101.5556 | 105.6667 | 109.7778 | 113.8889 | 118 | 122.8 | 127.6 | 132.4 | 137.2 | 142
5 | 0 | 5000 | 32 | 33.4 | 34.8 | 36.2 | 37.6 | 39 | 40.4 | 41.8 | 43.2 | 44.6 | 46 | 47.8 | 49.6 | 51.4 | 53.2 | 55 | 57.2 | 59.4 | 61.6 | 63.8 | 66 | 68.6 | 71.2 | 73.8 | 76.4 | 79 | 81.8 | 84.6 | 87.4 | 90.2 | 93
5 | 0.4 | 5004 | 32 | 33.4 | 34.8 | 36.2 | 37.6 | 39 | 40.4 | 41.8 | 43.2 | 44.6 | 46 | 47.8 | 49.6 | 51.4 | 53.2 | 55 | 57.2 | 59.4 | 61.6 | 63.8 | 66 | 68.6 | 71.2 | 73.8 | 76.4 | 79 | 81.8 | 84.6 | 87.4 | 90.2 | 93
5 | 0.6 | 5006 | 33 | 34.4 | 35.8 | 37.2 | 38.6 | 40 | 41.6 | 43.2 | 44.8 | 46.4 | 48 | 49.8 | 51.6 | 53.4 | 55.2 | 57 | 59.2 | 61.4 | 63.6 | 65.8 | 68 | 70.6 | 73.2 | 75.8 | 78.4 | 81 | 84.2 | 87.4 | 90.6 | 93.8 | 97
5 | 0.8 | 5008 | 34 | 35.4 | 36.8 | 38.2 | 39.6 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49 | 50.8 | 52.6 | 54.4 | 56.2 | 58 | 60.4 | 62.8 | 65.2 | 67.6 | 70 | 72.8 | 75.6 | 78.4 | 81.2 | 84 | 87.2 | 90.4 | 93.6 | 96.8 | 100
5 | 1 | 5010 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42 | 43.6 | 45.2 | 46.8 | 48.4 | 50 | 52 | 54 | 56 | 58 | 60 | 62.4 | 64.8 | 67.2 | 69.6 | 72 | 75 | 78 | 81 | 84 | 87 | 90.4 | 93.8 | 97.2 | 100.6 | 104
5 | 1.2 | 5012 | 36 | 37.2 | 38.4 | 39.6 | 40.8 | 42 | 43.8 | 45.6 | 47.4 | 49.2 | 51 | 53 | 55 | 57 | 59 | 61 | 63.6 | 66.2 | 68.8 | 71.4 | 74 | 77 | 80 | 83 | 86 | 89 | 92.6 | 96.2 | 99.8 | 103.4 | 107
5 | 1.4 | 5014 | 36 | 37.4 | 38.8 | 40.2 | 41.6 | 43 | 44.8 | 46.6 | 48.4 | 50.2 | 52 | 54 | 56 | 58 | 60 | 62 | 64.8 | 67.6 | 70.4 | 73.2 | 76 | 79 | 82 | 85 | 88 | 91 | 94.8 | 98.6 | 102.4 | 106.2 | 110
5 | 1.6 | 5016 | 37 | 38.4 | 39.8 | 41.2 | 42.6 | 44 | 45.8 | 47.6 | 49.4 | 51.2 | 53 | 55.2 | 57.4 | 59.6 | 61.8 | 64 | 66.6 | 69.2 | 71.8 | 74.4 | 77 | 80.4 | 83.8 | 87.2 | 90.6 | 94 | 97.6 | 101.2 | 104.8 | 108.4 | 112
5 | 1.8 | 5018 | 38 | 39.4 | 40.8 | 42.2 | 43.6 | 45 | 46.8 | 48.6 | 50.4 | 52.2 | 54 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.8 | 70.6 | 73.4 | 76.2 | 79 | 82.4 | 85.8 | 89.2 | 92.6 | 96 | 99.8 | 103.6 | 107.4 | 111.2 | 115
5 | 2 | 5020 | 39 | 40.4 | 41.8 | 43.2 | 44.6 | 46 | 47.8 | 49.6 | 51.4 | 53.2 | 55 | 57.4 | 59.8 | 62.2 | 64.6 | 67 | 69.8 | 72.6 | 75.4 | 78.2 | 81 | 84.4 | 87.8 | 91.2 | 94.6 | 98 | 102 | 106 | 110 | 114 | 118
5 | 2.2 | 5022 | 39 | 40.6 | 42.2 | 43.8 | 45.4 | 47 | 48.8 | 50.6 | 52.4 | 54.2 | 56 | 58.4 | 60.8 | 63.2 | 65.6 | 68 | 71 | 74 | 77 | 80 | 83 | 86.4 | 89.8 | 93.2 | 96.6 | 100 | 104 | 108 | 112 | 116 | 120
5 | 2.4 | 5024 | 40 | 41.6 | 43.2 | 44.8 | 46.4 | 48 | 49.8 | 51.6 | 53.4 | 55.2 | 57 | 59.6 | 62.2 | 64.8 | 67.4 | 70 | 72.8 | 75.6 | 78.4 | 81.2 | 84 | 87.6 | 91.2 | 94.8 | 98.4 | 102 | 106.2 | 110.4 | 114.6 | 118.8 | 123
5 | 2.6 | 5026 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49 | 50.8 | 52.6 | 54.4 | 56.2 | 58 | 60.6 | 63.2 | 65.8 | 68.4 | 71 | 74 | 77 | 80 | 83 | 86 | 89.6 | 93.2 | 96.8 | 100.4 | 104 | 108.2 | 112.4 | 116.6 | 120.8 | 125
5 | 2.8 | 5028 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49 | 51 | 53 | 55 | 57 | 59 | 61.6 | 64.2 | 66.8 | 69.4 | 72 | 75.2 | 78.4 | 81.6 | 84.8 | 88 | 91.6 | 95.2 | 98.8 | 102.4 | 106 | 110.2 | 114.4 | 118.6 | 122.8 | 127
5 | 3 | 5030 | 42 | 43.6 | 45.2 | 46.8 | 48.4 | 50 | 52.2 | 54.4 | 56.6 | 58.8 | 61 | 63.6 | 66.2 | 68.8 | 71.4 | 74 | 77 | 80 | 83 | 86 | 89 | 92.8 | 96.6 | 100.4 | 104.2 | 108 | 112.4 | 116.8 | 121.2 | 125.6 | 130
6 | 0 | 6000 | 30.4 | 31.72 | 33.04 | 34.36 | 35.68 | 37 | 38.36 | 39.72 | 41.08 | 42.44 | 43.8 | 45.52 | 47.24 | 48.96 | 50.68 | 52.4 | 54.48 | 56.56 | 58.64 | 60.72 | 62.8 | 65.24 | 67.68 | 70.12 | 72.56 | 75 | 77.68 | 80.36 | 83.04 | 85.72 | 88.4
6 | 0.4 | 6004 | 30.4 | 31.72 | 33.04 | 34.36 | 35.68 | 37 | 38.36 | 39.72 | 41.08 | 42.44 | 43.8 | 45.52 | 47.24 | 48.96 | 50.68 | 52.4 | 54.48 | 56.56 | 58.64 | 60.72 | 62.8 | 65.24 | 67.68 | 70.12 | 72.56 | 75 | 77.68 | 80.36 | 83.04 | 85.72 | 88.4
6 | 0.6 | 6006 | 31.4 | 32.72 | 34.04 | 35.36 | 36.68 | 38 | 39.52 | 41.04 | 42.56 | 44.08 | 45.6 | 47.32 | 49.04 | 50.76 | 52.48 | 54.2 | 56.28 | 58.36 | 60.44 | 62.52 | 64.6 | 67.08 | 69.56 | 72.04 | 74.52 | 77 | 80.04 | 83.08 | 86.12 | 89.16 | 92.2
6 | 0.8 | 6008 | 32.4 | 33.72 | 35.04 | 36.36 | 37.68 | 39 | 40.52 | 42.04 | 43.56 | 45.08 | 46.6 | 48.32 | 50.04 | 51.76 | 53.48 | 55.2 | 57.48 | 59.76 | 62.04 | 64.32 | 66.6 | 69.24 | 71.88 | 74.52 | 77.16 | 79.8 | 82.84 | 85.88 | 88.92 | 91.96 | 95
6 | 1 | 6010 | 33.2 | 34.52 | 35.84 | 37.16 | 38.48 | 39.8 | 41.32 | 42.84 | 44.36 | 45.88 | 47.4 | 49.32 | 51.24 | 53.16 | 55.08 | 57 | 59.28 | 61.56 | 63.84 | 66.12 | 68.4 | 71.24 | 74.08 | 76.92 | 79.76 | 82.6 | 85.84 | 89.08 | 92.32 | 95.56 | 98.8
6 | 1.2 | 6012 | 34.2 | 35.36 | 36.52 | 37.68 | 38.84 | 40 | 41.68 | 43.36 | 45.04 | 46.72 | 48.4 | 50.32 | 52.24 | 54.16 | 56.08 | 58 | 60.44 | 62.88 | 65.32 | 67.76 | 70.2 | 73.08 | 75.96 | 78.84 | 81.72 | 84.6 | 88 | 91.4 | 94.8 | 98.2 | 101.6
6 | 1.4 | 6014 | 34.2 | 35.56 | 36.92 | 38.28 | 39.64 | 41 | 42.68 | 44.36 | 46.04 | 47.72 | 49.4 | 51.32 | 53.24 | 55.16 | 57.08 | 59 | 61.64 | 64.28 | 66.92 | 69.56 | 72.2 | 75.08 | 77.96 | 80.84 | 83.72 | 86.6 | 90.16 | 93.72 | 97.28 | 100.84 | 104.4
6 | 1.6 | 6016 | 35.2 | 36.52 | 37.84 | 39.16 | 40.48 | 41.8 | 43.52 | 45.24 | 46.96 | 48.68 | 50.4 | 52.48 | 54.56 | 56.64 | 58.72 | 60.8 | 63.28 | 65.76 | 68.24 | 70.72 | 73.2 | 76.4 | 79.6 | 82.8 | 86 | 89.2 | 92.64 | 96.08 | 99.52 | 102.96 | 106.4
6 | 1.8 | 6018 | 36.2 | 37.52 | 38.84 | 40.16 | 41.48 | 42.8 | 44.52 | 46.24 | 47.96 | 49.68 | 51.4 | 53.48 | 55.56 | 57.64 | 59.72 | 61.8 | 64.48 | 67.16 | 69.84 | 72.52 | 75.2 | 78.4 | 81.6 | 84.8 | 88 | 91.2 | 94.8 | 98.4 | 102 | 105.6 | 109.2
6 | 2 | 6020 | 37 | 38.36 | 39.72 | 41.08 | 42.44 | 43.8 | 45.48 | 47.16 | 48.84 | 50.52 | 52.2 | 54.48 | 56.76 | 59.04 | 61.32 | 63.6 | 66.28 | 68.96 | 71.64 | 74.32 | 77 | 80.24 | 83.48 | 86.72 | 89.96 | 93.2 | 96.96 | 100.72 | 104.48 | 108.24 | 112
6 | 2.2 | 6022 | 37.2 | 38.68 | 40.16 | 41.64 | 43.12 | 44.6 | 46.32 | 48.04 | 49.76 | 51.48 | 53.2 | 55.48 | 57.76 | 60.04 | 62.32 | 64.6 | 67.44 | 70.28 | 73.12 | 75.96 | 78.8 | 82.04 | 85.28 | 88.52 | 91.76 | 95 | 98.8 | 102.6 | 106.4 | 110.2 | 114
6 | 2.4 | 6024 | 38 | 39.52 | 41.04 | 42.56 | 44.08 | 45.6 | 47.32 | 49.04 | 50.76 | 52.48 | 54.2 | 56.64 | 59.08 | 61.52 | 63.96 | 66.4 | 69.08 | 71.76 | 74.44 | 77.12 | 79.8 | 83.24 | 86.68 | 90.12 | 93.56 | 97 | 100.96 | 104.92 | 108.88 | 112.84 | 116.8
6 | 2.6 | 6026 | 39 | 40.52 | 42.04 | 43.56 | 45.08 | 46.6 | 48.32 | 50.04 | 51.76 | 53.48 | 55.2 | 57.64 | 60.08 | 62.52 | 64.96 | 67.4 | 70.28 | 73.16 | 76.04 | 78.92 | 81.8 | 85.2 | 88.6 | 92 | 95.4 | 98.8 | 102.8 | 106.8 | 110.8 | 114.8 | 118.8
6 | 2.8 | 6028 | 39 | 40.52 | 42.04 | 43.56 | 45.08 | 46.6 | 48.52 | 50.44 | 52.36 | 54.28 | 56.2 | 58.64 | 61.08 | 63.52 | 65.96 | 68.4 | 71.44 | 74.48 | 77.52 | 80.56 | 83.6 | 87.04 | 90.48 | 93.92 | 97.36 | 100.8 | 104.8 | 108.8 | 112.8 | 116.8 | 120.8
6 | 3 | 6030 | 40 | 41.52 | 43.04 | 44.56 | 46.08 | 47.6 | 49.68 | 51.76 | 53.84 | 55.92 | 58 | 60.44 | 62.88 | 65.32 | 67.76 | 70.2 | 73.08 | 75.96 | 78.84 | 81.72 | 84.6 | 88.2 | 91.8 | 95.4 | 99 | 102.6 | 106.76 | 110.92 | 115.08 | 119.24 | 123.4
7 | 0 | 7000 | 28.8 | 30.04 | 31.28 | 32.52 | 33.76 | 35 | 36.32 | 37.64 | 38.96 | 40.28 | 41.6 | 43.24 | 44.88 | 46.52 | 48.16 | 49.8 | 51.76 | 53.72 | 55.68 | 57.64 | 59.6 | 61.88 | 64.16 | 66.44 | 68.72 | 71 | 73.56 | 76.12 | 78.68 | 81.24 | 83.8
7 | 0.4 | 7004 | 28.8 | 30.04 | 31.28 | 32.52 | 33.76 | 35 | 36.32 | 37.64 | 38.96 | 40.28 | 41.6 | 43.24 | 44.88 | 46.52 | 48.16 | 49.8 | 51.76 | 53.72 | 55.68 | 57.64 | 59.6 | 61.88 | 64.16 | 66.44 | 68.72 | 71 | 73.56 | 76.12 | 78.68 | 81.24 | 83.8
7 | 0.6 | 7006 | 29.8 | 31.04 | 32.28 | 33.52 | 34.76 | 36 | 37.44 | 38.88 | 40.32 | 41.76 | 43.2 | 44.84 | 46.48 | 48.12 | 49.76 | 51.4 | 53.36 | 55.32 | 57.28 | 59.24 | 61.2 | 63.56 | 65.92 | 68.28 | 70.64 | 73 | 75.88 | 78.76 | 81.64 | 84.52 | 87.4
7 | 0.8 | 7008 | 30.8 | 32.04 | 33.28 | 34.52 | 35.76 | 37 | 38.44 | 39.88 | 41.32 | 42.76 | 44.2 | 45.84 | 47.48 | 49.12 | 50.76 | 52.4 | 54.56 | 56.72 | 58.88 | 61.04 | 63.2 | 65.68 | 68.16 | 70.64 | 73.12 | 75.6 | 78.48 | 81.36 | 84.24 | 87.12 | 90
7 | 1 | 7010 | 31.4 | 32.64 | 33.88 | 35.12 | 36.36 | 37.6 | 39.04 | 40.48 | 41.92 | 43.36 | 44.8 | 46.64 | 48.48 | 50.32 | 52.16 | 54 | 56.16 | 58.32 | 60.48 | 62.64 | 64.8 | 67.48 | 70.16 | 72.84 | 75.52 | 78.2 | 81.28 | 84.36 | 87.44 | 90.52 | 93.6
7 | 1.2 | 7012 | 32.4 | 33.52 | 34.64 | 35.76 | 36.88 | 38 | 39.56 | 41.12 | 42.68 | 44.24 | 45.8 | 47.64 | 49.48 | 51.32 | 53.16 | 55 | 57.28 | 59.56 | 61.84 | 64.12 | 66.4 | 69.16 | 71.92 | 74.68 | 77.44 | 80.2 | 83.4 | 86.6 | 89.8 | 93 | 96.2
7 | 1.4 | 7014 | 32.4 | 33.72 | 35.04 | 36.36 | 37.68 | 39 | 40.56 | 42.12 | 43.68 | 45.24 | 46.8 | 48.64 | 50.48 | 52.32 | 54.16 | 56 | 58.48 | 60.96 | 63.44 | 65.92 | 68.4 | 71.16 | 73.92 | 76.68 | 79.44 | 82.2 | 85.52 | 88.84 | 92.16 | 95.48 | 98.8
7 | 1.6 | 7016 | 33.4 | 34.64 | 35.88 | 37.12 | 38.36 | 39.6 | 41.24 | 42.88 | 44.52 | 46.16 | 47.8 | 49.76 | 51.72 | 53.68 | 55.64 | 57.6 | 59.96 | 62.32 | 64.68 | 67.04 | 69.4 | 72.4 | 75.4 | 78.4 | 81.4 | 84.4 | 87.68 | 90.96 | 94.24 | 97.52 | 100.8
7 | 1.8 | 7018 | 34.4 | 35.64 | 36.88 | 38.12 | 39.36 | 40.6 | 42.24 | 43.88 | 45.52 | 47.16 | 48.8 | 50.76 | 52.72 | 54.68 | 56.64 | 58.6 | 61.16 | 63.72 | 66.28 | 68.84 | 71.4 | 74.4 | 77.4 | 80.4 | 83.4 | 86.4 | 89.8 | 93.2 | 96.6 | 100 | 103.4
7 | 2 | 7020 | 35 | 36.32 | 37.64 | 38.96 | 40.28 | 41.6 | 43.16 | 44.72 | 46.28 | 47.84 | 49.4 | 51.56 | 53.72 | 55.88 | 58.04 | 60.2 | 62.76 | 65.32 | 67.88 | 70.44 | 73 | 76.08 | 79.16 | 82.24 | 85.32 | 88.4 | 91.92 | 95.44 | 98.96 | 102.48 | 106
7 | 2.2 | 7022 | 35.4 | 36.76 | 38.12 | 39.48 | 40.84 | 42.2 | 43.84 | 45.48 | 47.12 | 48.76 | 50.4 | 52.56 | 54.72 | 56.88 | 59.04 | 61.2 | 63.88 | 66.56 | 69.24 | 71.92 | 74.6 | 77.68 | 80.76 | 83.84 | 86.92 | 90 | 93.6 | 97.2 | 100.8 | 104.4 | 108
7 | 2.4 | 7024 | 36 | 37.44 | 38.88 | 40.32 | 41.76 | 43.2 | 44.84 | 46.48 | 48.12 | 49.76 | 51.4 | 53.68 | 55.96 | 58.24 | 60.52 | 62.8 | 65.36 | 67.92 | 70.48 | 73.04 | 75.6 | 78.88 | 82.16 | 85.44 | 88.72 | 92 | 95.72 | 99.44 | 103.16 | 106.88 | 110.6
7 | 2.6 | 7026 | 37 | 38.44 | 39.88 | 41.32 | 42.76 | 44.2 | 45.84 | 47.48 | 49.12 | 50.76 | 52.4 | 54.68 | 56.96 | 59.24 | 61.52 | 63.8 | 66.56 | 69.32 | 72.08 | 74.84 | 77.6 | 80.8 | 84 | 87.2 | 90.4 | 93.6 | 97.4 | 101.2 | 105 | 108.8 | 112.6
7 | 2.8 | 7028 | 37 | 38.44 | 39.88 | 41.32 | 42.76 | 44.2 | 46.04 | 47.88 | 49.72 | 51.56 | 53.4 | 55.68 | 57.96 | 60.24 | 62.52 | 64.8 | 67.68 | 70.56 | 73.44 | 76.32 | 79.2 | 82.48 | 85.76 | 89.04 | 92.32 | 95.6 | 99.4 | 103.2 | 107 | 110.8 | 114.6
7 | 3 | 7030 | 38 | 39.44 | 40.88 | 42.32 | 43.76 | 45.2 | 47.16 | 49.12 | 51.08 | 53.04 | 55 | 57.28 | 59.56 | 61.84 | 64.12 | 66.4 | 69.16 | 71.92 | 74.68 | 77.44 | 80.2 | 83.6 | 87 | 90.4 | 93.8 | 97.2 | 101.12 | 105.04 | 108.96 | 112.88 | 116.8
8 | 0 | 8000 | 27.2 | 28.36 | 29.52 | 30.68 | 31.84 | 33 | 34.28 | 35.56 | 36.84 | 38.12 | 39.4 | 40.96 | 42.52 | 44.08 | 45.64 | 47.2 | 49.04 | 50.88 | 52.72 | 54.56 | 56.4 | 58.52 | 60.64 | 62.76 | 64.88 | 67 | 69.44 | 71.88 | 74.32 | 76.76 | 79.2
8 | 0.4 | 8004 | 27.2 | 28.36 | 29.52 | 30.68 | 31.84 | 33 | 34.28 | 35.56 | 36.84 | 38.12 | 39.4 | 40.96 | 42.52 | 44.08 | 45.64 | 47.2 | 49.04 | 50.88 | 52.72 | 54.56 | 56.4 | 58.52 | 60.64 | 62.76 | 64.88 | 67 | 69.44 | 71.88 | 74.32 | 76.76 | 79.2
8 | 0.6 | 8006 | 28.2 | 29.36 | 30.52 | 31.68 | 32.84 | 34 | 35.36 | 36.72 | 38.08 | 39.44 | 40.8 | 42.36 | 43.92 | 45.48 | 47.04 | 48.6 | 50.44 | 52.28 | 54.12 | 55.96 | 57.8 | 60.04 | 62.28 | 64.52 | 66.76 | 69 | 71.72 | 74.44 | 77.16 | 79.88 | 82.6
8 | 0.8 | 8008 | 29.2 | 30.36 | 31.52 | 32.68 | 33.84 | 35 | 36.36 | 37.72 | 39.08 | 40.44 | 41.8 | 43.36 | 44.92 | 46.48 | 48.04 | 49.6 | 51.64 | 53.68 | 55.72 | 57.76 | 59.8 | 62.12 | 64.44 | 66.76 | 69.08 | 71.4 | 74.12 | 76.84 | 79.56 | 82.28 | 85
8 | 1 | 8010 | 29.6 | 30.76 | 31.92 | 33.08 | 34.24 | 35.4 | 36.76 | 38.12 | 39.48 | 40.84 | 42.2 | 43.96 | 45.72 | 47.48 | 49.24 | 51 | 53.04 | 55.08 | 57.12 | 59.16 | 61.2 | 63.72 | 66.24 | 68.76 | 71.28 | 73.8 | 76.72 | 79.64 | 82.56 | 85.48 | 88.4
8 | 1.2 | 8012 | 30.6 | 31.68 | 32.76 | 33.84 | 34.92 | 36 | 37.44 | 38.88 | 40.32 | 41.76 | 43.2 | 44.96 | 46.72 | 48.48 | 50.24 | 52 | 54.12 | 56.24 | 58.36 | 60.48 | 62.6 | 65.24 | 67.88 | 70.52 | 73.16 | 75.8 | 78.8 | 81.8 | 84.8 | 87.8 | 90.8
8 | 1.4 | 8014 | 30.6 | 31.88 | 33.16 | 34.44 | 35.72 | 37 | 38.44 | 39.88 | 41.32 | 42.76 | 44.2 | 45.96 | 47.72 | 49.48 | 51.24 | 53 | 55.32 | 57.64 | 59.96 | 62.28 | 64.6 | 67.24 | 69.88 | 72.52 | 75.16 | 77.8 | 80.88 | 83.96 | 87.04 | 90.12 | 93.2
8 | 1.6 | 8016 | 31.6 | 32.76 | 33.92 | 35.08 | 36.24 | 37.4 | 38.96 | 40.52 | 42.08 | 43.64 | 45.2 | 47.04 | 48.88 | 50.72 | 52.56 | 54.4 | 56.64 | 58.88 | 61.12 | 63.36 | 65.6 | 68.4 | 71.2 | 74 | 76.8 | 79.6 | 82.72 | 85.84 | 88.96 | 92.08 | 95.2
8 | 1.8 | 8018 | 32.6 | 33.76 | 34.92 | 36.08 | 37.24 | 38.4 | 39.96 | 41.52 | 43.08 | 44.64 | 46.2 | 48.04 | 49.88 | 51.72 | 53.56 | 55.4 | 57.84 | 60.28 | 62.72 | 65.16 | 67.6 | 70.4 | 73.2 | 76 | 78.8 | 81.6 | 84.8 | 88 | 91.2 | 94.4 | 97.6
8 | 2 | 8020 | 33 | 34.28 | 35.56 | 36.84 | 38.12 | 39.4 | 40.84 | 42.28 | 43.72 | 45.16 | 46.6 | 48.64 | 50.68 | 52.72 | 54.76 | 56.8 | 59.24 | 61.68 | 64.12 | 66.56 | 69 | 71.92 | 74.84 | 77.76 | 80.68 | 83.6 | 86.88 | 90.16 | 93.44 | 96.72 | 100
8 | 2.2 | 8022 | 33.6 | 34.84 | 36.08 | 37.32 | 38.56 | 39.8 | 41.36 | 42.92 | 44.48 | 46.04 | 47.6 | 49.64 | 51.68 | 53.72 | 55.76 | 57.8 | 60.32 | 62.84 | 65.36 | 67.88 | 70.4 | 73.32 | 76.24 | 79.16 | 82.08 | 85 | 88.4 | 91.8 | 95.2 | 98.6 | 102
8 | 2.4 | 8024 | 34 | 35.36 | 36.72 | 38.08 | 39.44 | 40.8 | 42.36 | 43.92 | 45.48 | 47.04 | 48.6 | 50.72 | 52.84 | 54.96 | 57.08 | 59.2 | 61.64 | 64.08 | 66.52 | 68.96 | 71.4 | 74.52 | 77.64 | 80.76 | 83.88 | 87 | 90.48 | 93.96 | 97.44 | 100.92 | 104.4
8 | 2.6 | 8026 | 35 | 36.36 | 37.72 | 39.08 | 40.44 | 41.8 | 43.36 | 44.92 | 46.48 | 48.04 | 49.6 | 51.72 | 53.84 | 55.96 | 58.08 | 60.2 | 62.84 | 65.48 | 68.12 | 70.76 | 73.4 | 76.4 | 79.4 | 82.4 | 85.4 | 88.4 | 92 | 95.6 | 99.2 | 102.8 | 106.4
8 | 2.8 | 8028 | 35 | 36.36 | 37.72 | 39.08 | 40.44 | 41.8 | 43.56 | 45.32 | 47.08 | 48.84 | 50.6 | 52.72 | 54.84 | 56.96 | 59.08 | 61.2 | 63.92 | 66.64 | 69.36 | 72.08 | 74.8 | 77.92 | 81.04 | 84.16 | 87.28 | 90.4 | 94 | 97.6 | 101.2 | 104.8 | 108.4
8 | 3 | 8030 | 36 | 37.36 | 38.72 | 40.08 | 41.44 | 42.8 | 44.64 | 46.48 | 48.32 | 50.16 | 52 | 54.12 | 56.24 | 58.36 | 60.48 | 62.6 | 65.24 | 67.88 | 70.52 | 73.16 | 75.8 | 79 | 82.2 | 85.4 | 88.6 | 91.8 | 95.48 | 99.16 | 102.84 | 106.52 | 110.2
9 | 0 | 9000 | 25.6 | 26.68 | 27.76 | 28.84 | 29.92 | 31 | 32.24 | 33.48 | 34.72 | 35.96 | 37.2 | 38.68 | 40.16 | 41.64 | 43.12 | 44.6 | 46.32 | 48.04 | 49.76 | 51.48 | 53.2 | 55.16 | 57.12 | 59.08 | 61.04 | 63 | 65.32 | 67.64 | 69.96 | 72.28 | 74.6
9 | 0.4 | 9004 | 25.6 | 26.68 | 27.76 | 28.84 | 29.92 | 31 | 32.24 | 33.48 | 34.72 | 35.96 | 37.2 | 38.68 | 40.16 | 41.64 | 43.12 | 44.6 | 46.32 | 48.04 | 49.76 | 51.48 | 53.2 | 55.16 | 57.12 | 59.08 | 61.04 | 63 | 65.32 | 67.64 | 69.96 | 72.28 | 74.6
9 | 0.6 | 9006 | 26.6 | 27.68 | 28.76 | 29.84 | 30.92 | 32 | 33.28 | 34.56 | 35.84 | 37.12 | 38.4 | 39.88 | 41.36 | 42.84 | 44.32 | 45.8 | 47.52 | 49.24 | 50.96 | 52.68 | 54.4 | 56.52 | 58.64 | 60.76 | 62.88 | 65 | 67.56 | 70.12 | 72.68 | 75.24 | 77.8
9 | 0.8 | 9008 | 27.6 | 28.68 | 29.76 | 30.84 | 31.92 | 33 | 34.28 | 35.56 | 36.84 | 38.12 | 39.4 | 40.88 | 42.36 | 43.84 | 45.32 | 46.8 | 48.72 | 50.64 | 52.56 | 54.48 | 56.4 | 58.56 | 60.72 | 62.88 | 65.04 | 67.2 | 69.76 | 72.32 | 74.88 | 77.44 | 80
9 | 1 | 9010 | 27.8 | 28.88 | 29.96 | 31.04 | 32.12 | 33.2 | 34.48 | 35.76 | 37.04 | 38.32 | 39.6 | 41.28 | 42.96 | 44.64 | 46.32 | 48 | 49.92 | 51.84 | 53.76 | 55.68 | 57.6 | 59.96 | 62.32 | 64.68 | 67.04 | 69.4 | 72.16 | 74.92 | 77.68 | 80.44 | 83.2
9 | 1.2 | 9012 | 28.8 | 29.84 | 30.88 | 31.92 | 32.96 | 34 | 35.32 | 36.64 | 37.96 | 39.28 | 40.6 | 42.28 | 43.96 | 45.64 | 47.32 | 49 | 50.96 | 52.92 | 54.88 | 56.84 | 58.8 | 61.32 | 63.84 | 66.36 | 68.88 | 71.4 | 74.2 | 77 | 79.8 | 82.6 | 85.4
9 | 1.4 | 9014 | 28.8 | 30.04 | 31.28 | 32.52 | 33.76 | 35 | 36.32 | 37.64 | 38.96 | 40.28 | 41.6 | 43.28 | 44.96 | 46.64 | 48.32 | 50 | 52.16 | 54.32 | 56.48 | 58.64 | 60.8 | 63.32 | 65.84 | 68.36 | 70.88 | 73.4 | 76.24 | 79.08 | 81.92 | 84.76 | 87.6
9 | 1.6 | 9016 | 29.8 | 30.88 | 31.96 | 33.04 | 34.12 | 35.2 | 36.68 | 38.16 | 39.64 | 41.12 | 42.6 | 44.32 | 46.04 | 47.76 | 49.48 | 51.2 | 53.32 | 55.44 | 57.56 | 59.68 | 61.8 | 64.4 | 67 | 69.6 | 72.2 | 74.8 | 77.76 | 80.72 | 83.68 | 86.64 | 89.6
9 | 1.8 | 9018 | 30.8 | 31.88 | 32.96 | 34.04 | 35.12 | 36.2 | 37.68 | 39.16 | 40.64 | 42.12 | 43.6 | 45.32 | 47.04 | 48.76 | 50.48 | 52.2 | 54.52 | 56.84 | 59.16 | 61.48 | 63.8 | 66.4 | 69 | 71.6 | 74.2 | 76.8 | 79.8 | 82.8 | 85.8 | 88.8 | 91.8
9 | 2 | 9020 | 31 | 32.24 | 33.48 | 34.72 | 35.96 | 37.2 | 38.52 | 39.84 | 41.16 | 42.48 | 43.8 | 45.72 | 47.64 | 49.56 | 51.48 | 53.4 | 55.72 | 58.04 | 60.36 | 62.68 | 65 | 67.76 | 70.52 | 73.28 | 76.04 | 78.8 | 81.84 | 84.88 | 87.92 | 90.96 | 94
9 | 2.2 | 9022 | 31.8 | 32.92 | 34.04 | 35.16 | 36.28 | 37.4 | 38.88 | 40.36 | 41.84 | 43.32 | 44.8 | 46.72 | 48.64 | 50.56 | 52.48 | 54.4 | 56.76 | 59.12 | 61.48 | 63.84 | 66.2 | 68.96 | 71.72 | 74.48 | 77.24 | 80 | 83.2 | 86.4 | 89.6 | 92.8 | 96
9 | 2.4 | 9024 | 32 | 33.28 | 34.56 | 35.84 | 37.12 | 38.4 | 39.88 | 41.36 | 42.84 | 44.32 | 45.8 | 47.76 | 49.72 | 51.68 | 53.64 | 55.6 | 57.92 | 60.24 | 62.56 | 64.88 | 67.2 | 70.16 | 73.12 | 76.08 | 79.04 | 82 | 85.24 | 88.48 | 91.72 | 94.96 | 98.2
9 | 2.6 | 9026 | 33 | 34.28 | 35.56 | 36.84 | 38.12 | 39.4 | 40.88 | 42.36 | 43.84 | 45.32 | 46.8 | 48.76 | 50.72 | 52.68 | 54.64 | 56.6 | 59.12 | 61.64 | 64.16 | 66.68 | 69.2 | 72 | 74.8 | 77.6 | 80.4 | 83.2 | 86.6 | 90 | 93.4 | 96.8 | 100.2
9 | 2.8 | 9028 | 33 | 34.28 | 35.56 | 36.84 | 38.12 | 39.4 | 41.08 | 42.76 | 44.44 | 46.12 | 47.8 | 49.76 | 51.72 | 53.68 | 55.64 | 57.6 | 60.16 | 62.72 | 65.28 | 67.84 | 70.4 | 73.36 | 76.32 | 79.28 | 82.24 | 85.2 | 88.6 | 92 | 95.4 | 98.8 | 102.2
9 | 3 | 9030 | 34 | 35.28 | 36.56 | 37.84 | 39.12 | 40.4 | 42.12 | 43.84 | 45.56 | 47.28 | 49 | 50.96 | 52.92 | 54.88 | 56.84 | 58.8 | 61.32 | 63.84 | 66.36 | 68.88 | 71.4 | 74.4 | 77.4 | 80.4 | 83.4 | 86.4 | 89.84 | 93.28 | 96.72 | 100.16 | 103.6
10 | 0 | 10000 | 24 | 25 | 26 | 27 | 28 | 29 | 30.2 | 31.4 | 32.6 | 33.8 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42 | 43.6 | 45.2 | 46.8 | 48.4 | 50 | 51.8 | 53.6 | 55.4 | 57.2 | 59 | 61.2 | 63.4 | 65.6 | 67.8 | 70
10 | 0.4 | 10004 | 24 | 25 | 26 | 27 | 28 | 29 | 30.2 | 31.4 | 32.6 | 33.8 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42 | 43.6 | 45.2 | 46.8 | 48.4 | 50 | 51.8 | 53.6 | 55.4 | 57.2 | 59 | 61.2 | 63.4 | 65.6 | 67.8 | 70
10 | 0.6 | 10006 | 25 | 26 | 27 | 28 | 29 | 30 | 31.2 | 32.4 | 33.6 | 34.8 | 36 | 37.4 | 38.8 | 40.2 | 41.6 | 43 | 44.6 | 46.2 | 47.8 | 49.4 | 51 | 53 | 55 | 57 | 59 | 61 | 63.4 | 65.8 | 68.2 | 70.6 | 73
10 | 0.8 | 10008 | 26 | 27 | 28 | 29 | 30 | 31 | 32.2 | 33.4 | 34.6 | 35.8 | 37 | 38.4 | 39.8 | 41.2 | 42.6 | 44 | 45.8 | 47.6 | 49.4 | 51.2 | 53 | 55 | 57 | 59 | 61 | 63 | 65.4 | 67.8 | 70.2 | 72.6 | 75
10 | 1 | 10010 | 26 | 27 | 28 | 29 | 30 | 31 | 32.2 | 33.4 | 34.6 | 35.8 | 37 | 38.6 | 40.2 | 41.8 | 43.4 | 45 | 46.8 | 48.6 | 50.4 | 52.2 | 54 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.6 | 70.2 | 72.8 | 75.4 | 78
10 | 1.2 | 10012 | 27 | 28 | 29 | 30 | 31 | 32 | 33.2 | 34.4 | 35.6 | 36.8 | 38 | 39.6 | 41.2 | 42.8 | 44.4 | 46 | 47.8 | 49.6 | 51.4 | 53.2 | 55 | 57.4 | 59.8 | 62.2 | 64.6 | 67 | 69.6 | 72.2 | 74.8 | 77.4 | 80
10 | 1.4 | 10014 | 27 | 28.2 | 29.4 | 30.6 | 31.8 | 33 | 34.2 | 35.4 | 36.6 | 37.8 | 39 | 40.6 | 42.2 | 43.8 | 45.4 | 47 | 49 | 51 | 53 | 55 | 57 | 59.4 | 61.8 | 64.2 | 66.6 | 69 | 71.6 | 74.2 | 76.8 | 79.4 | 82
10 | 1.6 | 10016 | 28 | 29 | 30 | 31 | 32 | 33 | 34.4 | 35.8 | 37.2 | 38.6 | 40 | 41.6 | 43.2 | 44.8 | 46.4 | 48 | 50 | 52 | 54 | 56 | 58 | 60.4 | 62.8 | 65.2 | 67.6 | 70 | 72.8 | 75.6 | 78.4 | 81.2 | 84
10 | 1.8 | 10018 | 29 | 30 | 31 | 32 | 33 | 34 | 35.4 | 36.8 | 38.2 | 39.6 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49 | 51.2 | 53.4 | 55.6 | 57.8 | 60 | 62.4 | 64.8 | 67.2 | 69.6 | 72 | 74.8 | 77.6 | 80.4 | 83.2 | 86
10 | 2 | 10020 | 29 | 30.2 | 31.4 | 32.6 | 33.8 | 35 | 36.2 | 37.4 | 38.6 | 39.8 | 41 | 42.8 | 44.6 | 46.4 | 48.2 | 50 | 52.2 | 54.4 | 56.6 | 58.8 | 61 | 63.6 | 66.2 | 68.8 | 71.4 | 74 | 76.8 | 79.6 | 82.4 | 85.2 | 88
10 | 2.2 | 10022 | 30 | 31 | 32 | 33 | 34 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42 | 43.8 | 45.6 | 47.4 | 49.2 | 51 | 53.2 | 55.4 | 57.6 | 59.8 | 62 | 64.6 | 67.2 | 69.8 | 72.4 | 75 | 78 | 81 | 84 | 87 | 90
10 | 2.4 | 10024 | 30 | 31.2 | 32.4 | 33.6 | 34.8 | 36 | 37.4 | 38.8 | 40.2 | 41.6 | 43 | 44.8 | 46.6 | 48.4 | 50.2 | 52 | 54.2 | 56.4 | 58.6 | 60.8 | 63 | 65.8 | 68.6 | 71.4 | 74.2 | 77 | 80 | 83 | 86 | 89 | 92
10 | 2.6 | 10026 | 31 | 32.2 | 33.4 | 34.6 | 35.8 | 37 | 38.4 | 39.8 | 41.2 | 42.6 | 44 | 45.8 | 47.6 | 49.4 | 51.2 | 53 | 55.4 | 57.8 | 60.2 | 62.6 | 65 | 67.6 | 70.2 | 72.8 | 75.4 | 78 | 81.2 | 84.4 | 87.6 | 90.8 | 94
10 | 2.8 | 10028 | 31 | 32.2 | 33.4 | 34.6 | 35.8 | 37 | 38.6 | 40.2 | 41.8 | 43.4 | 45 | 46.8 | 48.6 | 50.4 | 52.2 | 54 | 56.4 | 58.8 | 61.2 | 63.6 | 66 | 68.8 | 71.6 | 74.4 | 77.2 | 80 | 83.2 | 86.4 | 89.6 | 92.8 | 96
10 | 3 | 10030 | 32 | 33.2 | 34.4 | 35.6 | 36.8 | 38 | 39.6 | 41.2 | 42.8 | 44.4 | 46 | 47.8 | 49.6 | 51.4 | 53.2 | 55 | 57.4 | 59.8 | 62.2 | 64.6 | 67 | 69.8 | 72.6 | 75.4 | 78.2 | 81 | 84.2 | 87.4 | 90.6 | 93.8 | 97
11 | 0 | 11000 | 22.4 | 23.36 | 24.32 | 25.28 | 26.24 | 27.2 | 28.28 | 29.36 | 30.44 | 31.52 | 32.6 | 33.92 | 35.24 | 36.56 | 37.88 | 39.2 | 40.68 | 42.16 | 43.64 | 45.12 | 46.6 | 48.28 | 49.96 | 51.64 | 53.32 | 55 | 57.08 | 59.16 | 61.24 | 63.32 | 65.4
11 | 0.4 | 11004 | 22.4 | 23.36 | 24.32 | 25.28 | 26.24 | 27.2 | 28.28 | 29.36 | 30.44 | 31.52 | 32.6 | 33.92 | 35.24 | 36.56 | 37.88 | 39.2 | 40.68 | 42.16 | 43.64 | 45.12 | 46.6 | 48.28 | 49.96 | 51.64 | 53.32 | 55 | 57.08 | 59.16 | 61.24 | 63.32 | 65.4
11 | 0.6 | 11006 | 23.4 | 24.32 | 25.24 | 26.16 | 27.08 | 28 | 29.12 | 30.24 | 31.36 | 32.48 | 33.6 | 34.92 | 36.24 | 37.56 | 38.88 | 40.2 | 41.68 | 43.16 | 44.64 | 46.12 | 47.6 | 49.48 | 51.36 | 53.24 | 55.12 | 57 | 59.24 | 61.48 | 63.72 | 65.96 | 68.2
11 | 0.8 | 11008 | 24.2 | 25.12 | 26.04 | 26.96 | 27.88 | 28.8 | 29.92 | 31.04 | 32.16 | 33.28 | 34.4 | 35.72 | 37.04 | 38.36 | 39.68 | 41 | 42.68 | 44.36 | 46.04 | 47.72 | 49.4 | 51.28 | 53.16 | 55.04 | 56.92 | 58.8 | 61.04 | 63.28 | 65.52 | 67.76 | 70
11 | 1 | 11010 | 24.4 | 25.32 | 26.24 | 27.16 | 28.08 | 29 | 30.12 | 31.24 | 32.36 | 33.48 | 34.6 | 36.08 | 37.56 | 39.04 | 40.52 | 42 | 43.68 | 45.36 | 47.04 | 48.72 | 50.4 | 52.44 | 54.48 | 56.52 | 58.56 | 60.6 | 63.04 | 65.48 | 67.92 | 70.36 | 72.8
11 | 1.2 | 11012 | 25.2 | 26.12 | 27.04 | 27.96 | 28.88 | 29.8 | 30.92 | 32.04 | 33.16 | 34.28 | 35.4 | 36.92 | 38.44 | 39.96 | 41.48 | 43 | 44.68 | 46.36 | 48.04 | 49.72 | 51.4 | 53.64 | 55.88 | 58.12 | 60.36 | 62.6 | 65 | 67.4 | 69.8 | 72.2 | 74.6
11 | 1.4 | 11014 | 25.2 | 26.32 | 27.44 | 28.56 | 29.68 | 30.8 | 31.92 | 33.04 | 34.16 | 35.28 | 36.4 | 37.88 | 39.36 | 40.84 | 42.32 | 43.8 | 45.68 | 47.56 | 49.44 | 51.32 | 53.2 | 55.44 | 57.68 | 59.92 | 62.16 | 64.4 | 66.84 | 69.28 | 71.72 | 74.16 | 76.6
11 | 1.6 | 11016 | 26.2 | 27.12 | 28.04 | 28.96 | 29.88 | 30.8 | 32.08 | 33.36 | 34.64 | 35.92 | 37.2 | 38.72 | 40.24 | 41.76 | 43.28 | 44.8 | 46.68 | 48.56 | 50.44 | 52.32 | 54.2 | 56.44 | 58.68 | 60.92 | 63.16 | 65.4 | 68 | 70.6 | 73.2 | 75.8 | 78.4
11 | 1.8 | 11018 | 27 | 27.96 | 28.92 | 29.88 | 30.84 | 31.8 | 33.08 | 34.36 | 35.64 | 36.92 | 38.2 | 39.72 | 41.24 | 42.76 | 44.28 | 45.8 | 47.84 | 49.88 | 51.92 | 53.96 | 56 | 58.24 | 60.48 | 62.72 | 64.96 | 67.2 | 69.84 | 72.48 | 75.12 | 77.76 | 80.4
11 | 2 | 11020 | 27 | 28.12 | 29.24 | 30.36 | 31.48 | 32.6 | 33.76 | 34.92 | 36.08 | 37.24 | 38.4 | 40.04 | 41.68 | 43.32 | 44.96 | 46.6 | 48.68 | 50.76 | 52.84 | 54.92 | 57 | 59.4 | 61.8 | 64.2 | 66.6 | 69 | 71.64 | 74.28 | 76.92 | 79.56 | 82.2
11 | 2.2 | 11022 | 28 | 28.92 | 29.84 | 30.76 | 31.68 | 32.6 | 33.92 | 35.24 | 36.56 | 37.88 | 39.2 | 40.88 | 42.56 | 44.24 | 45.92 | 47.6 | 49.64 | 51.68 | 53.72 | 55.76 | 57.8 | 60.24 | 62.68 | 65.12 | 67.56 | 70 | 72.8 | 75.6 | 78.4 | 81.2 | 84
11 | 2.4 | 11024 | 28 | 29.12 | 30.24 | 31.36 | 32.48 | 33.6 | 34.92 | 36.24 | 37.56 | 38.88 | 40.2 | 41.88 | 43.56 | 45.24 | 46.92 | 48.6 | 50.64 | 52.68 | 54.72 | 56.76 | 58.8 | 61.4 | 64 | 66.6 | 69.2 | 71.8 | 74.6 | 77.4 | 80.2 | 83 | 85.8
11 | 2.6 | 11026 | 28.8 | 29.92 | 31.04 | 32.16 | 33.28 | 34.4 | 35.72 | 37.04 | 38.36 | 39.68 | 41 | 42.72 | 44.44 | 46.16 | 47.88 | 49.6 | 51.8 | 54 | 56.2 | 58.4 | 60.6 | 63.04 | 65.48 | 67.92 | 70.36 | 72.8 | 75.8 | 78.8 | 81.8 | 84.8 | 87.8
11 | 2.8 | 11028 | 29 | 30.12 | 31.24 | 32.36 | 33.48 | 34.6 | 36.08 | 37.56 | 39.04 | 40.52 | 42 | 43.68 | 45.36 | 47.04 | 48.72 | 50.4 | 52.64 | 54.88 | 57.12 | 59.36 | 61.6 | 64.2 | 66.8 | 69.4 | 72 | 74.6 | 77.6 | 80.6 | 83.6 | 86.6 | 89.6
11 | 3 | 11030 | 29.8 | 30.92 | 32.04 | 33.16 | 34.28 | 35.4 | 36.88 | 38.36 | 39.84 | 41.32 | 42.8 | 44.52 | 46.24 | 47.96 | 49.68 | 51.4 | 53.64 | 55.88 | 58.12 | 60.36 | 62.6 | 65.2 | 67.8 | 70.4 | 73 | 75.6 | 78.6 | 81.6 | 84.6 | 87.6 | 90.6
12 | 0 | 12000 | 20.8 | 21.72 | 22.64 | 23.56 | 24.48 | 25.4 | 26.36 | 27.32 | 28.28 | 29.24 | 30.2 | 31.44 | 32.68 | 33.92 | 35.16 | 36.4 | 37.76 | 39.12 | 40.48 | 41.84 | 43.2 | 44.76 | 46.32 | 47.88 | 49.44 | 51 | 52.96 | 54.92 | 56.88 | 58.84 | 60.8
12 | 0.4 | 12004 | 20.8 | 21.72 | 22.64 | 23.56 | 24.48 | 25.4 | 26.36 | 27.32 | 28.28 | 29.24 | 30.2 | 31.44 | 32.68 | 33.92 | 35.16 | 36.4 | 37.76 | 39.12 | 40.48 | 41.84 | 43.2 | 44.76 | 46.32 | 47.88 | 49.44 | 51 | 52.96 | 54.92 | 56.88 | 58.84 | 60.8
12 | 0.6 | 12006 | 21.8 | 22.64 | 23.48 | 24.32 | 25.16 | 26 | 27.04 | 28.08 | 29.12 | 30.16 | 31.2 | 32.44 | 33.68 | 34.92 | 36.16 | 37.4 | 38.76 | 40.12 | 41.48 | 42.84 | 44.2 | 45.96 | 47.72 | 49.48 | 51.24 | 53 | 55.08 | 57.16 | 59.24 | 61.32 | 63.4
12 | 0.8 | 12008 | 22.4 | 23.24 | 24.08 | 24.92 | 25.76 | 26.6 | 27.64 | 28.68 | 29.72 | 30.76 | 31.8 | 33.04 | 34.28 | 35.52 | 36.76 | 38 | 39.56 | 41.12 | 42.68 | 44.24 | 45.8 | 47.56 | 49.32 | 51.08 | 52.84 | 54.6 | 56.68 | 58.76 | 60.84 | 62.92 | 65
12 | 1 | 12010 | 22.8 | 23.64 | 24.48 | 25.32 | 26.16 | 27 | 28.04 | 29.08 | 30.12 | 31.16 | 32.2 | 33.56 | 34.92 | 36.28 | 37.64 | 39 | 40.56 | 42.12 | 43.68 | 45.24 | 46.8 | 48.68 | 50.56 | 52.44 | 54.32 | 56.2 | 58.48 | 60.76 | 63.04 | 65.32 | 67.6
12 | 1.2 | 12012 | 23.4 | 24.24 | 25.08 | 25.92 | 26.76 | 27.6 | 28.64 | 29.68 | 30.72 | 31.76 | 32.8 | 34.24 | 35.68 | 37.12 | 38.56 | 40 | 41.56 | 43.12 | 44.68 | 46.24 | 47.8 | 49.88 | 51.96 | 54.04 | 56.12 | 58.2 | 60.4 | 62.6 | 64.8 | 67 | 69.2
12 | 1.4 | 12014 | 23.4 | 24.44 | 25.48 | 26.52 | 27.56 | 28.6 | 29.64 | 30.68 | 31.72 | 32.76 | 33.8 | 35.16 | 36.52 | 37.88 | 39.24 | 40.6 | 42.36 | 44.12 | 45.88 | 47.64 | 49.4 | 51.48 | 53.56 | 55.64 | 57.72 | 59.8 | 62.08 | 64.36 | 66.64 | 68.92 | 71.2
12 | 1.6 | 12016 | 24.4 | 25.24 | 26.08 | 26.92 | 27.76 | 28.6 | 29.76 | 30.92 | 32.08 | 33.24 | 34.4 | 35.84 | 37.28 | 38.72 | 40.16 | 41.6 | 43.36 | 45.12 | 46.88 | 48.64 | 50.4 | 52.48 | 54.56 | 56.64 | 58.72 | 60.8 | 63.2 | 65.6 | 68 | 70.4 | 72.8
12 | 1.8 | 12018 | 25 | 25.92 | 26.84 | 27.76 | 28.68 | 29.6 | 30.76 | 31.92 | 33.08 | 34.24 | 35.4 | 36.84 | 38.28 | 39.72 | 41.16 | 42.6 | 44.48 | 46.36 | 48.24 | 50.12 | 52 | 54.08 | 56.16 | 58.24 | 60.32 | 62.4 | 64.88 | 67.36 | 69.84 | 72.32 | 74.8
12 | 2 | 12020 | 25 | 26.04 | 27.08 | 28.12 | 29.16 | 30.2 | 31.32 | 32.44 | 33.56 | 34.68 | 35.8 | 37.28 | 38.76 | 40.24 | 41.72 | 43.2 | 45.16 | 47.12 | 49.08 | 51.04 | 53 | 55.2 | 57.4 | 59.6 | 61.8 | 64 | 66.48 | 68.96 | 71.44 | 73.92 | 76.4
12 | 2.2 | 12022 | 26 | 26.84 | 27.68 | 28.52 | 29.36 | 30.2 | 31.44 | 32.68 | 33.92 | 35.16 | 36.4 | 37.96 | 39.52 | 41.08 | 42.64 | 44.2 | 46.08 | 47.96 | 49.84 | 51.72 | 53.6 | 55.88 | 58.16 | 60.44 | 62.72 | 65 | 67.6 | 70.2 | 72.8 | 75.4 | 78
12 | 2.4 | 12024 | 26 | 27.04 | 28.08 | 29.12 | 30.16 | 31.2 | 32.44 | 33.68 | 34.92 | 36.16 | 37.4 | 38.96 | 40.52 | 42.08 | 43.64 | 45.2 | 47.08 | 48.96 | 50.84 | 52.72 | 54.6 | 57 | 59.4 | 61.8 | 64.2 | 66.6 | 69.2 | 71.8 | 74.4 | 77 | 79.6
12 | 2.6 | 12026 | 26.6 | 27.64 | 28.68 | 29.72 | 30.76 | 31.8 | 33.04 | 34.28 | 35.52 | 36.76 | 38 | 39.64 | 41.28 | 42.92 | 44.56 | 46.2 | 48.2 | 50.2 | 52.2 | 54.2 | 56.2 | 58.48 | 60.76 | 63.04 | 65.32 | 67.6 | 70.4 | 73.2 | 76 | 78.8 | 81.6
12 | 2.8 | 12028 | 27 | 28.04 | 29.08 | 30.12 | 31.16 | 32.2 | 33.56 | 34.92 | 36.28 | 37.64 | 39 | 40.56 | 42.12 | 43.68 | 45.24 | 46.8 | 48.88 | 50.96 | 53.04 | 55.12 | 57.2 | 59.6 | 62 | 64.4 | 66.8 | 69.2 | 72 | 74.8 | 77.6 | 80.4 | 83.2
12 | 3 | 12030 | 27.6 | 28.64 | 29.68 | 30.72 | 31.76 | 32.8 | 34.16 | 35.52 | 36.88 | 38.24 | 39.6 | 41.24 | 42.88 | 44.52 | 46.16 | 47.8 | 49.88 | 51.96 | 54.04 | 56.12 | 58.2 | 60.6 | 63 | 65.4 | 67.8 | 70.2 | 73 | 75.8 | 78.6 | 81.4 | 84.2
13 | 0 | 13000 | 19.2 | 20.08 | 20.96 | 21.84 | 22.72 | 23.6 | 24.44 | 25.28 | 26.12 | 26.96 | 27.8 | 28.96 | 30.12 | 31.28 | 32.44 | 33.6 | 34.84 | 36.08 | 37.32 | 38.56 | 39.8 | 41.24 | 42.68 | 44.12 | 45.56 | 47 | 48.84 | 50.68 | 52.52 | 54.36 | 56.2
13 | 0.4 | 13004 | 19.2 | 20.08 | 20.96 | 21.84 | 22.72 | 23.6 | 24.44 | 25.28 | 26.12 | 26.96 | 27.8 | 28.96 | 30.12 | 31.28 | 32.44 | 33.6 | 34.84 | 36.08 | 37.32 | 38.56 | 39.8 | 41.24 | 42.68 | 44.12 | 45.56 | 47 | 48.84 | 50.68 | 52.52 | 54.36 | 56.2
13 | 0.6 | 13006 | 20.2 | 20.96 | 21.72 | 22.48 | 23.24 | 24 | 24.96 | 25.92 | 26.88 | 27.84 | 28.8 | 29.96 | 31.12 | 32.28 | 33.44 | 34.6 | 35.84 | 37.08 | 38.32 | 39.56 | 40.8 | 42.44 | 44.08 | 45.72 | 47.36 | 49 | 50.92 | 52.84 | 54.76 | 56.68 | 58.6
13 | 0.8 | 13008 | 20.6 | 21.36 | 22.12 | 22.88 | 23.64 | 24.4 | 25.36 | 26.32 | 27.28 | 28.24 | 29.2 | 30.36 | 31.52 | 32.68 | 33.84 | 35 | 36.44 | 37.88 | 39.32 | 40.76 | 42.2 | 43.84 | 45.48 | 47.12 | 48.76 | 50.4 | 52.32 | 54.24 | 56.16 | 58.08 | 60
13 | 1 | 13010 | 21.2 | 21.96 | 22.72 | 23.48 | 24.24 | 25 | 25.96 | 26.92 | 27.88 | 28.84 | 29.8 | 31.04 | 32.28 | 33.52 | 34.76 | 36 | 37.44 | 38.88 | 40.32 | 41.76 | 43.2 | 44.92 | 46.64 | 48.36 | 50.08 | 51.8 | 53.92 | 56.04 | 58.16 | 60.28 | 62.4
13 | 1.2 | 13012 | 21.6 | 22.36 | 23.12 | 23.88 | 24.64 | 25.4 | 26.36 | 27.32 | 28.28 | 29.24 | 30.2 | 31.56 | 32.92 | 34.28 | 35.64 | 37 | 38.44 | 39.88 | 41.32 | 42.76 | 44.2 | 46.12 | 48.04 | 49.96 | 51.88 | 53.8 | 55.8 | 57.8 | 59.8 | 61.8 | 63.8
13 | 1.4 | 13014 | 21.6 | 22.56 | 23.52 | 24.48 | 25.44 | 26.4 | 27.36 | 28.32 | 29.28 | 30.24 | 31.2 | 32.44 | 33.68 | 34.92 | 36.16 | 37.4 | 39.04 | 40.68 | 42.32 | 43.96 | 45.6 | 47.52 | 49.44 | 51.36 | 53.28 | 55.2 | 57.32 | 59.44 | 61.56 | 63.68 | 65.8
13 | 1.6 | 13016 | 22.6 | 23.36 | 24.12 | 24.88 | 25.64 | 26.4 | 27.44 | 28.48 | 29.52 | 30.56 | 31.6 | 32.96 | 34.32 | 35.68 | 37.04 | 38.4 | 40.04 | 41.68 | 43.32 | 44.96 | 46.6 | 48.52 | 50.44 | 52.36 | 54.28 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.2
13 | 1.8 | 13018 | 23 | 23.88 | 24.76 | 25.64 | 26.52 | 27.4 | 28.44 | 29.48 | 30.52 | 31.56 | 32.6 | 33.96 | 35.32 | 36.68 | 38.04 | 39.4 | 41.12 | 42.84 | 44.56 | 46.28 | 48 | 49.92 | 51.84 | 53.76 | 55.68 | 57.6 | 59.92 | 62.24 | 64.56 | 66.88 | 69.2
13 | 2 | 13020 | 23 | 23.96 | 24.92 | 25.88 | 26.84 | 27.8 | 28.88 | 29.96 | 31.04 | 32.12 | 33.2 | 34.52 | 35.84 | 37.16 | 38.48 | 39.8 | 41.64 | 43.48 | 45.32 | 47.16 | 49 | 51 | 53 | 55 | 57 | 59 | 61.32 | 63.64 | 65.96 | 68.28 | 70.6
13 | 2.2 | 13022 | 24 | 24.76 | 25.52 | 26.28 | 27.04 | 27.8 | 28.96 | 30.12 | 31.28 | 32.44 | 33.6 | 35.04 | 36.48 | 37.92 | 39.36 | 40.8 | 42.52 | 44.24 | 45.96 | 47.68 | 49.4 | 51.52 | 53.64 | 55.76 | 57.88 | 60 | 62.4 | 64.8 | 67.2 | 69.6 | 72
13 | 2.4 | 13024 | 24 | 24.96 | 25.92 | 26.88 | 27.84 | 28.8 | 29.96 | 31.12 | 32.28 | 33.44 | 34.6 | 36.04 | 37.48 | 38.92 | 40.36 | 41.8 | 43.52 | 45.24 | 46.96 | 48.68 | 50.4 | 52.6 | 54.8 | 57 | 59.2 | 61.4 | 63.8 | 66.2 | 68.6 | 71 | 73.4
13 | 2.6 | 13026 | 24.4 | 25.36 | 26.32 | 27.28 | 28.24 | 29.2 | 30.36 | 31.52 | 32.68 | 33.84 | 35 | 36.56 | 38.12 | 39.68 | 41.24 | 42.8 | 44.6 | 46.4 | 48.2 | 50 | 51.8 | 53.92 | 56.04 | 58.16 | 60.28 | 62.4 | 65 | 67.6 | 70.2 | 72.8 | 75.4
13 | 2.8 | 13028 | 25 | 25.96 | 26.92 | 27.88 | 28.84 | 29.8 | 31.04 | 32.28 | 33.52 | 34.76 | 36 | 37.44 | 38.88 | 40.32 | 41.76 | 43.2 | 45.12 | 47.04 | 48.96 | 50.88 | 52.8 | 55 | 57.2 | 59.4 | 61.6 | 63.8 | 66.4 | 69 | 71.6 | 74.2 | 76.8
13 | 3 | 13030 | 25.4 | 26.36 | 27.32 | 28.28 | 29.24 | 30.2 | 31.44 | 32.68 | 33.92 | 35.16 | 36.4 | 37.96 | 39.52 | 41.08 | 42.64 | 44.2 | 46.12 | 48.04 | 49.96 | 51.88 | 53.8 | 56 | 58.2 | 60.4 | 62.6 | 64.8 | 67.4 | 70 | 72.6 | 75.2 | 77.8
14 | 0 | 14000 | 17.6 | 18.44 | 19.28 | 20.12 | 20.96 | 21.8 | 22.52 | 23.24 | 23.96 | 24.68 | 25.4 | 26.48 | 27.56 | 28.64 | 29.72 | 30.8 | 31.92 | 33.04 | 34.16 | 35.28 | 36.4 | 37.72 | 39.04 | 40.36 | 41.68 | 43 | 44.72 | 46.44 | 48.16 | 49.88 | 51.6
14 | 0.4 | 14004 | 17.6 | 18.44 | 19.28 | 20.12 | 20.96 | 21.8 | 22.52 | 23.24 | 23.96 | 24.68 | 25.4 | 26.48 | 27.56 | 28.64 | 29.72 | 30.8 | 31.92 | 33.04 | 34.16 | 35.28 | 36.4 | 37.72 | 39.04 | 40.36 | 41.68 | 43 | 44.72 | 46.44 | 48.16 | 49.88 | 51.6
14 | 0.6 | 14006 | 18.6 | 19.28 | 19.96 | 20.64 | 21.32 | 22 | 22.88 | 23.76 | 24.64 | 25.52 | 26.4 | 27.48 | 28.56 | 29.64 | 30.72 | 31.8 | 32.92 | 34.04 | 35.16 | 36.28 | 37.4 | 38.92 | 40.44 | 41.96 | 43.48 | 45 | 46.76 | 48.52 | 50.28 | 52.04 | 53.8
14 | 0.8 | 14008 | 18.8 | 19.48 | 20.16 | 20.84 | 21.52 | 22.2 | 23.08 | 23.96 | 24.84 | 25.72 | 26.6 | 27.68 | 28.76 | 29.84 | 30.92 | 32 | 33.32 | 34.64 | 35.96 | 37.28 | 38.6 | 40.12 | 41.64 | 43.16 | 44.68 | 46.2 | 47.96 | 49.72 | 51.48 | 53.24 | 55
14 | 1 | 14010 | 19.6 | 20.28 | 20.96 | 21.64 | 22.32 | 23 | 23.88 | 24.76 | 25.64 | 26.52 | 27.4 | 28.52 | 29.64 | 30.76 | 31.88 | 33 | 34.32 | 35.64 | 36.96 | 38.28 | 39.6 | 41.16 | 42.72 | 44.28 | 45.84 | 47.4 | 49.36 | 51.32 | 53.28 | 55.24 | 57.2
14 | 1.2 | 14012 | 19.8 | 20.48 | 21.16 | 21.84 | 22.52 | 23.2 | 24.08 | 24.96 | 25.84 | 26.72 | 27.6 | 28.88 | 30.16 | 31.44 | 32.72 | 34 | 35.32 | 36.64 | 37.96 | 39.28 | 40.6 | 42.36 | 44.12 | 45.88 | 47.64 | 49.4 | 51.2 | 53 | 54.8 | 56.6 | 58.4
14 | 1.4 | 14014 | 19.8 | 20.68 | 21.56 | 22.44 | 23.32 | 24.2 | 25.08 | 25.96 | 26.84 | 27.72 | 28.6 | 29.72 | 30.84 | 31.96 | 33.08 | 34.2 | 35.72 | 37.24 | 38.76 | 40.28 | 41.8 | 43.56 | 45.32 | 47.08 | 48.84 | 50.6 | 52.56 | 54.52 | 56.48 | 58.44 | 60.4
14 | 1.6 | 14016 | 20.8 | 21.48 | 22.16 | 22.84 | 23.52 | 24.2 | 25.12 | 26.04 | 26.96 | 27.88 | 28.8 | 30.08 | 31.36 | 32.64 | 33.92 | 35.2 | 36.72 | 38.24 | 39.76 | 41.28 | 42.8 | 44.56 | 46.32 | 48.08 | 49.84 | 51.6 | 53.6 | 55.6 | 57.6 | 59.6 | 61.6
14 | 1.8 | 14018 | 21 | 21.84 | 22.68 | 23.52 | 24.36 | 25.2 | 26.12 | 27.04 | 27.96 | 28.88 | 29.8 | 31.08 | 32.36 | 33.64 | 34.92 | 36.2 | 37.76 | 39.32 | 40.88 | 42.44 | 44 | 45.76 | 47.52 | 49.28 | 51.04 | 52.8 | 54.96 | 57.12 | 59.28 | 61.44 | 63.6
14 | 2 | 14020 | 21 | 21.88 | 22.76 | 23.64 | 24.52 | 25.4 | 26.44 | 27.48 | 28.52 | 29.56 | 30.6 | 31.76 | 32.92 | 34.08 | 35.24 | 36.4 | 38.12 | 39.84 | 41.56 | 43.28 | 45 | 46.8 | 48.6 | 50.4 | 52.2 | 54 | 56.16 | 58.32 | 60.48 | 62.64 | 64.8
14 | 2.2 | 14022 | 22 | 22.68 | 23.36 | 24.04 | 24.72 | 25.4 | 26.48 | 27.56 | 28.64 | 29.72 | 30.8 | 32.12 | 33.44 | 34.76 | 36.08 | 37.4 | 38.96 | 40.52 | 42.08 | 43.64 | 45.2 | 47.16 | 49.12 | 51.08 | 53.04 | 55 | 57.2 | 59.4 | 61.6 | 63.8 | 66
14 | 2.4 | 14024 | 22 | 22.88 | 23.76 | 24.64 | 25.52 | 26.4 | 27.48 | 28.56 | 29.64 | 30.72 | 31.8 | 33.12 | 34.44 | 35.76 | 37.08 | 38.4 | 39.96 | 41.52 | 43.08 | 44.64 | 46.2 | 48.2 | 50.2 | 52.2 | 54.2 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 67.2
14 | 2.6 | 14026 | 22.2 | 23.08 | 23.96 | 24.84 | 25.72 | 26.6 | 27.68 | 28.76 | 29.84 | 30.92 | 32 | 33.48 | 34.96 | 36.44 | 37.92 | 39.4 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49.36 | 51.32 | 53.28 | 55.24 | 57.2 | 59.6 | 62 | 64.4 | 66.8 | 69.2
14 | 2.8 | 14028 | 23 | 23.88 | 24.76 | 25.64 | 26.52 | 27.4 | 28.52 | 29.64 | 30.76 | 31.88 | 33 | 34.32 | 35.64 | 36.96 | 38.28 | 39.6 | 41.36 | 43.12 | 44.88 | 46.64 | 48.4 | 50.4 | 52.4 | 54.4 | 56.4 | 58.4 | 60.8 | 63.2 | 65.6 | 68 | 70.4
14 | 3 | 14030 | 23.2 | 24.08 | 24.96 | 25.84 | 26.72 | 27.6 | 28.72 | 29.84 | 30.96 | 32.08 | 33.2 | 34.68 | 36.16 | 37.64 | 39.12 | 40.6 | 42.36 | 44.12 | 45.88 | 47.64 | 49.4 | 51.4 | 53.4 | 55.4 | 57.4 | 59.4 | 61.8 | 64.2 | 66.6 | 69 | 71.4
15 | 0 | 15000 | 16 | 16.8 | 17.6 | 18.4 | 19.2 | 20 | 20.6 | 21.2 | 21.8 | 22.4 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34.2 | 35.4 | 36.6 | 37.8 | 39 | 40.6 | 42.2 | 43.8 | 45.4 | 47
15 | 0.4 | 15004 | 16 | 16.8 | 17.6 | 18.4 | 19.2 | 20 | 20.6 | 21.2 | 21.8 | 22.4 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34.2 | 35.4 | 36.6 | 37.8 | 39 | 40.6 | 42.2 | 43.8 | 45.4 | 47
15 | 0.6 | 15006 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.8 | 21.6 | 22.4 | 23.2 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35.4 | 36.8 | 38.2 | 39.6 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49
15 | 0.8 | 15008 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.8 | 21.6 | 22.4 | 23.2 | 24 | 25 | 26 | 27 | 28 | 29 | 30.2 | 31.4 | 32.6 | 33.8 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42 | 43.6 | 45.2 | 46.8 | 48.4 | 50
15 | 1 | 15010 | 18 | 18.6 | 19.2 | 19.8 | 20.4 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26 | 27 | 28 | 29 | 30 | 31.2 | 32.4 | 33.6 | 34.8 | 36 | 37.4 | 38.8 | 40.2 | 41.6 | 43 | 44.8 | 46.6 | 48.4 | 50.2 | 52
15 | 1.2 | 15012 | 18 | 18.6 | 19.2 | 19.8 | 20.4 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26.2 | 27.4 | 28.6 | 29.8 | 31 | 32.2 | 33.4 | 34.6 | 35.8 | 37 | 38.6 | 40.2 | 41.8 | 43.4 | 45 | 46.6 | 48.2 | 49.8 | 51.4 | 53
15 | 1.4 | 15014 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 22.8 | 23.6 | 24.4 | 25.2 | 26 | 27 | 28 | 29 | 30 | 31 | 32.4 | 33.8 | 35.2 | 36.6 | 38 | 39.6 | 41.2 | 42.8 | 44.4 | 46 | 47.8 | 49.6 | 51.4 | 53.2 | 55
15 | 1.6 | 15016 | 19 | 19.6 | 20.2 | 20.8 | 21.4 | 22 | 22.8 | 23.6 | 24.4 | 25.2 | 26 | 27.2 | 28.4 | 29.6 | 30.8 | 32 | 33.4 | 34.8 | 36.2 | 37.6 | 39 | 40.6 | 42.2 | 43.8 | 45.4 | 47 | 48.8 | 50.6 | 52.4 | 54.2 | 56
15 | 1.8 | 15018 | 19 | 19.8 | 20.6 | 21.4 | 22.2 | 23 | 23.8 | 24.6 | 25.4 | 26.2 | 27 | 28.2 | 29.4 | 30.6 | 31.8 | 33 | 34.4 | 35.8 | 37.2 | 38.6 | 40 | 41.6 | 43.2 | 44.8 | 46.4 | 48 | 50 | 52 | 54 | 56 | 58
15 | 2 | 15020 | 19 | 19.8 | 20.6 | 21.4 | 22.2 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34.6 | 36.2 | 37.8 | 39.4 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49 | 51 | 53 | 55 | 57 | 59
15 | 2.2 | 15022 | 20 | 20.6 | 21.2 | 21.8 | 22.4 | 23 | 24 | 25 | 26 | 27 | 28 | 29.2 | 30.4 | 31.6 | 32.8 | 34 | 35.4 | 36.8 | 38.2 | 39.6 | 41 | 42.8 | 44.6 | 46.4 | 48.2 | 50 | 52 | 54 | 56 | 58 | 60
15 | 2.4 | 15024 | 20 | 20.8 | 21.6 | 22.4 | 23.2 | 24 | 25 | 26 | 27 | 28 | 29 | 30.2 | 31.4 | 32.6 | 33.8 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42 | 43.8 | 45.6 | 47.4 | 49.2 | 51 | 53 | 55 | 57 | 59 | 61
15 | 2.6 | 15026 | 20 | 20.8 | 21.6 | 22.4 | 23.2 | 24 | 25 | 26 | 27 | 28 | 29 | 30.4 | 31.8 | 33.2 | 34.6 | 36 | 37.4 | 38.8 | 40.2 | 41.6 | 43 | 44.8 | 46.6 | 48.4 | 50.2 | 52 | 54.2 | 56.4 | 58.6 | 60.8 | 63
15 | 2.8 | 15028 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26 | 27 | 28 | 29 | 30 | 31.2 | 32.4 | 33.6 | 34.8 | 36 | 37.6 | 39.2 | 40.8 | 42.4 | 44 | 45.8 | 47.6 | 49.4 | 51.2 | 53 | 55.2 | 57.4 | 59.6 | 61.8 | 64
15 | 3 | 15030 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26 | 27 | 28 | 29 | 30 | 31.4 | 32.8 | 34.2 | 35.6 | 37 | 38.6 | 40.2 | 41.8 | 43.4 | 45 | 46.8 | 48.6 | 50.4 | 52.2 | 54 | 56.2 | 58.4 | 60.6 | 62.8 | 65
16 | 0 | 16000 | 15.2 | 15.96 | 16.72 | 17.48 | 18.24 | 19 | 19.56 | 20.12 | 20.68 | 21.24 | 21.8 | 22.76 | 23.72 | 24.68 | 25.64 | 26.6 | 27.56 | 28.52 | 29.48 | 30.44 | 31.4 | 32.56 | 33.72 | 34.88 | 36.04 | 37.2 | 38.68 | 40.16 | 41.64 | 43.12 | 44.6
16 | 0.4 | 16004 | 15.2 | 15.96 | 16.72 | 17.48 | 18.24 | 19 | 19.56 | 20.12 | 20.68 | 21.24 | 21.8 | 22.76 | 23.72 | 24.68 | 25.64 | 26.6 | 27.56 | 28.52 | 29.48 | 30.44 | 31.4 | 32.56 | 33.72 | 34.88 | 36.04 | 37.2 | 38.68 | 40.16 | 41.64 | 43.12 | 44.6
16 | 0.6 | 16006 | 16.2 | 16.76 | 17.32 | 17.88 | 18.44 | 19 | 19.76 | 20.52 | 21.28 | 22.04 | 22.8 | 23.72 | 24.64 | 25.56 | 26.48 | 27.4 | 28.4 | 29.4 | 30.4 | 31.4 | 32.4 | 33.72 | 35.04 | 36.36 | 37.68 | 39 | 40.48 | 41.96 | 43.44 | 44.92 | 46.4
16 | 0.8 | 16008 | 16.2 | 16.76 | 17.32 | 17.88 | 18.44 | 19 | 19.76 | 20.52 | 21.28 | 22.04 | 22.8 | 23.76 | 24.72 | 25.68 | 26.64 | 27.6 | 28.72 | 29.84 | 30.96 | 32.08 | 33.2 | 34.56 | 35.92 | 37.28 | 38.64 | 40 | 41.52 | 43.04 | 44.56 | 46.08 | 47.6
16 | 1 | 16010 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.76 | 21.52 | 22.28 | 23.04 | 23.8 | 24.72 | 25.64 | 26.56 | 27.48 | 28.4 | 29.56 | 30.72 | 31.88 | 33.04 | 34.2 | 35.56 | 36.92 | 38.28 | 39.64 | 41 | 42.68 | 44.36 | 46.04 | 47.72 | 49.4
16 | 1.2 | 16012 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.76 | 21.52 | 22.28 | 23.04 | 23.8 | 24.92 | 26.04 | 27.16 | 28.28 | 29.4 | 30.56 | 31.72 | 32.88 | 34.04 | 35.2 | 36.68 | 38.16 | 39.64 | 41.12 | 42.6 | 44.16 | 45.72 | 47.28 | 48.84 | 50.4
16 | 1.4 | 16014 | 17.2 | 17.92 | 18.64 | 19.36 | 20.08 | 20.8 | 21.56 | 22.32 | 23.08 | 23.84 | 24.6 | 25.56 | 26.52 | 27.48 | 28.44 | 29.4 | 30.72 | 32.04 | 33.36 | 34.68 | 36 | 37.52 | 39.04 | 40.56 | 42.08 | 43.6 | 45.32 | 47.04 | 48.76 | 50.48 | 52.2
16 | 1.6 | 16016 | 18 | 18.6 | 19.2 | 19.8 | 20.4 | 21 | 21.76 | 22.52 | 23.28 | 24.04 | 24.8 | 25.92 | 27.04 | 28.16 | 29.28 | 30.4 | 31.72 | 33.04 | 34.36 | 35.68 | 37 | 38.52 | 40.04 | 41.56 | 43.08 | 44.6 | 46.32 | 48.04 | 49.76 | 51.48 | 53.2
16 | 1.8 | 16018 | 18 | 18.76 | 19.52 | 20.28 | 21.04 | 21.8 | 22.56 | 23.32 | 24.08 | 24.84 | 25.6 | 26.76 | 27.92 | 29.08 | 30.24 | 31.4 | 32.72 | 34.04 | 35.36 | 36.68 | 38 | 39.52 | 41.04 | 42.56 | 44.08 | 45.6 | 47.48 | 49.36 | 51.24 | 53.12 | 55
16 | 2 | 16020 | 18.2 | 18.92 | 19.64 | 20.36 | 21.08 | 21.8 | 22.76 | 23.72 | 24.68 | 25.64 | 26.6 | 27.56 | 28.52 | 29.48 | 30.44 | 31.4 | 32.88 | 34.36 | 35.84 | 37.32 | 38.8 | 40.36 | 41.92 | 43.48 | 45.04 | 46.6 | 48.48 | 50.36 | 52.24 | 54.12 | 56
16 | 2.2 | 16022 | 19 | 19.6 | 20.2 | 20.8 | 21.4 | 22 | 22.92 | 23.84 | 24.76 | 25.68 | 26.6 | 27.76 | 28.92 | 30.08 | 31.24 | 32.4 | 33.72 | 35.04 | 36.36 | 37.68 | 39 | 40.72 | 42.44 | 44.16 | 45.88 | 47.6 | 49.48 | 51.36 | 53.24 | 55.12 | 57
16 | 2.4 | 16024 | 19 | 19.76 | 20.52 | 21.28 | 22.04 | 22.8 | 23.76 | 24.72 | 25.68 | 26.64 | 27.6 | 28.72 | 29.84 | 30.96 | 32.08 | 33.2 | 34.56 | 35.92 | 37.28 | 38.64 | 40 | 41.68 | 43.36 | 45.04 | 46.72 | 48.4 | 50.32 | 52.24 | 54.16 | 56.08 | 58
16 | 2.6 | 16026 | 19 | 19.76 | 20.52 | 21.28 | 22.04 | 22.8 | 23.76 | 24.72 | 25.68 | 26.64 | 27.6 | 28.92 | 30.24 | 31.56 | 32.88 | 34.2 | 35.52 | 36.84 | 38.16 | 39.48 | 40.8 | 42.52 | 44.24 | 45.96 | 47.68 | 49.4 | 51.48 | 53.56 | 55.64 | 57.72 | 59.8
16 | 2.8 | 16028 | 20 | 20.76 | 21.52 | 22.28 | 23.04 | 23.8 | 24.72 | 25.64 | 26.56 | 27.48 | 28.4 | 29.56 | 30.72 | 31.88 | 33.04 | 34.2 | 35.72 | 37.24 | 38.76 | 40.28 | 41.8 | 43.52 | 45.24 | 46.96 | 48.68 | 50.4 | 52.48 | 54.56 | 56.64 | 58.72 | 60.8
16 | 3 | 16030 | 20 | 20.76 | 21.52 | 22.28 | 23.04 | 23.8 | 24.76 | 25.72 | 26.68 | 27.64 | 28.6 | 29.92 | 31.24 | 32.56 | 33.88 | 35.2 | 36.72 | 38.24 | 39.76 | 41.28 | 42.8 | 44.52 | 46.24 | 47.96 | 49.68 | 51.4 | 53.48 | 55.56 | 57.64 | 59.72 | 61.8
17 | 0 | 17000 | 14.4 | 15.12 | 15.84 | 16.56 | 17.28 | 18 | 18.52 | 19.04 | 19.56 | 20.08 | 20.6 | 21.52 | 22.44 | 23.36 | 24.28 | 25.2 | 26.12 | 27.04 | 27.96 | 28.88 | 29.8 | 30.92 | 32.04 | 33.16 | 34.28 | 35.4 | 36.76 | 38.12 | 39.48 | 40.84 | 42.2
17 | 0.4 | 17004 | 14.4 | 15.12 | 15.84 | 16.56 | 17.28 | 18 | 18.52 | 19.04 | 19.56 | 20.08 | 20.6 | 21.52 | 22.44 | 23.36 | 24.28 | 25.2 | 26.12 | 27.04 | 27.96 | 28.88 | 29.8 | 30.92 | 32.04 | 33.16 | 34.28 | 35.4 | 36.76 | 38.12 | 39.48 | 40.84 | 42.2
17 | 0.6 | 17006 | 15.4 | 15.92 | 16.44 | 16.96 | 17.48 | 18 | 18.72 | 19.44 | 20.16 | 20.88 | 21.6 | 22.44 | 23.28 | 24.12 | 24.96 | 25.8 | 26.8 | 27.8 | 28.8 | 29.8 | 30.8 | 32.04 | 33.28 | 34.52 | 35.76 | 37 | 38.36 | 39.72 | 41.08 | 42.44 | 43.8
17 | 0.8 | 17008 | 15.4 | 15.92 | 16.44 | 16.96 | 17.48 | 18 | 18.72 | 19.44 | 20.16 | 20.88 | 21.6 | 22.52 | 23.44 | 24.36 | 25.28 | 26.2 | 27.24 | 28.28 | 29.32 | 30.36 | 31.4 | 32.72 | 34.04 | 35.36 | 36.68 | 38 | 39.44 | 40.88 | 42.32 | 43.76 | 45.2
17 | 1 | 17010 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.72 | 20.44 | 21.16 | 21.88 | 22.6 | 23.44 | 24.28 | 25.12 | 25.96 | 26.8 | 27.92 | 29.04 | 30.16 | 31.28 | 32.4 | 33.72 | 35.04 | 36.36 | 37.68 | 39 | 40.56 | 42.12 | 43.68 | 45.24 | 46.8
17 | 1.2 | 17012 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.72 | 20.44 | 21.16 | 21.88 | 22.6 | 23.64 | 24.68 | 25.72 | 26.76 | 27.8 | 28.92 | 30.04 | 31.16 | 32.28 | 33.4 | 34.76 | 36.12 | 37.48 | 38.84 | 40.2 | 41.72 | 43.24 | 44.76 | 46.28 | 47.8
17 | 1.4 | 17014 | 16.4 | 17.04 | 17.68 | 18.32 | 18.96 | 19.6 | 20.32 | 21.04 | 21.76 | 22.48 | 23.2 | 24.12 | 25.04 | 25.96 | 26.88 | 27.8 | 29.04 | 30.28 | 31.52 | 32.76 | 34 | 35.44 | 36.88 | 38.32 | 39.76 | 41.2 | 42.84 | 44.48 | 46.12 | 47.76 | 49.4
17 | 1.6 | 17016 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.72 | 21.44 | 22.16 | 22.88 | 23.6 | 24.64 | 25.68 | 26.72 | 27.76 | 28.8 | 30.04 | 31.28 | 32.52 | 33.76 | 35 | 36.44 | 37.88 | 39.32 | 40.76 | 42.2 | 43.84 | 45.48 | 47.12 | 48.76 | 50.4
17 | 1.8 | 17018 | 17 | 17.72 | 18.44 | 19.16 | 19.88 | 20.6 | 21.32 | 22.04 | 22.76 | 23.48 | 24.2 | 25.32 | 26.44 | 27.56 | 28.68 | 29.8 | 31.04 | 32.28 | 33.52 | 34.76 | 36 | 37.44 | 38.88 | 40.32 | 41.76 | 43.2 | 44.96 | 46.72 | 48.48 | 50.24 | 52
17 | 2 | 17020 | 17.4 | 18.04 | 18.68 | 19.32 | 19.96 | 20.6 | 21.52 | 22.44 | 23.36 | 24.28 | 25.2 | 26.12 | 27.04 | 27.96 | 28.88 | 29.8 | 31.16 | 32.52 | 33.88 | 35.24 | 36.6 | 38.12 | 39.64 | 41.16 | 42.68 | 44.2 | 45.96 | 47.72 | 49.48 | 51.24 | 53
17 | 2.2 | 17022 | 18 | 18.6 | 19.2 | 19.8 | 20.4 | 21 | 21.84 | 22.68 | 23.52 | 24.36 | 25.2 | 26.32 | 27.44 | 28.56 | 29.68 | 30.8 | 32.04 | 33.28 | 34.52 | 35.76 | 37 | 38.64 | 40.28 | 41.92 | 43.56 | 45.2 | 46.96 | 48.72 | 50.48 | 52.24 | 54
17 | 2.4 | 17024 | 18 | 18.72 | 19.44 | 20.16 | 20.88 | 21.6 | 22.52 | 23.44 | 24.36 | 25.28 | 26.2 | 27.24 | 28.28 | 29.32 | 30.36 | 31.4 | 32.72 | 34.04 | 35.36 | 36.68 | 38 | 39.56 | 41.12 | 42.68 | 44.24 | 45.8 | 47.64 | 49.48 | 51.32 | 53.16 | 55
17 | 2.6 | 17026 | 18 | 18.72 | 19.44 | 20.16 | 20.88 | 21.6 | 22.52 | 23.44 | 24.36 | 25.28 | 26.2 | 27.44 | 28.68 | 29.92 | 31.16 | 32.4 | 33.64 | 34.88 | 36.12 | 37.36 | 38.6 | 40.24 | 41.88 | 43.52 | 45.16 | 46.8 | 48.76 | 50.72 | 52.68 | 54.64 | 56.6
17 | 2.8 | 17028 | 19 | 19.72 | 20.44 | 21.16 | 21.88 | 22.6 | 23.44 | 24.28 | 25.12 | 25.96 | 26.8 | 27.92 | 29.04 | 30.16 | 31.28 | 32.4 | 33.84 | 35.28 | 36.72 | 38.16 | 39.6 | 41.24 | 42.88 | 44.52 | 46.16 | 47.8 | 49.76 | 51.72 | 53.68 | 55.64 | 57.6
17 | 3 | 17030 | 19 | 19.72 | 20.44 | 21.16 | 21.88 | 22.6 | 23.52 | 24.44 | 25.36 | 26.28 | 27.2 | 28.44 | 29.68 | 30.92 | 32.16 | 33.4 | 34.84 | 36.28 | 37.72 | 39.16 | 40.6 | 42.24 | 43.88 | 45.52 | 47.16 | 48.8 | 50.76 | 52.72 | 54.68 | 56.64 | 58.6
18 | 0 | 18000 | 13.6 | 14.28 | 14.96 | 15.64 | 16.32 | 17 | 17.48 | 17.96 | 18.44 | 18.92 | 19.4 | 20.28 | 21.16 | 22.04 | 22.92 | 23.8 | 24.68 | 25.56 | 26.44 | 27.32 | 28.2 | 29.28 | 30.36 | 31.44 | 32.52 | 33.6 | 34.84 | 36.08 | 37.32 | 38.56 | 39.8
18 | 0.4 | 18004 | 13.6 | 14.28 | 14.96 | 15.64 | 16.32 | 17 | 17.48 | 17.96 | 18.44 | 18.92 | 19.4 | 20.28 | 21.16 | 22.04 | 22.92 | 23.8 | 24.68 | 25.56 | 26.44 | 27.32 | 28.2 | 29.28 | 30.36 | 31.44 | 32.52 | 33.6 | 34.84 | 36.08 | 37.32 | 38.56 | 39.8
18 | 0.6 | 18006 | 14.6 | 15.08 | 15.56 | 16.04 | 16.52 | 17 | 17.68 | 18.36 | 19.04 | 19.72 | 20.4 | 21.16 | 21.92 | 22.68 | 23.44 | 24.2 | 25.2 | 26.2 | 27.2 | 28.2 | 29.2 | 30.36 | 31.52 | 32.68 | 33.84 | 35 | 36.24 | 37.48 | 38.72 | 39.96 | 41.2
18 | 0.8 | 18008 | 14.6 | 15.08 | 15.56 | 16.04 | 16.52 | 17 | 17.68 | 18.36 | 19.04 | 19.72 | 20.4 | 21.28 | 22.16 | 23.04 | 23.92 | 24.8 | 25.76 | 26.72 | 27.68 | 28.64 | 29.6 | 30.88 | 32.16 | 33.44 | 34.72 | 36 | 37.36 | 38.72 | 40.08 | 41.44 | 42.8
18 | 1 | 18010 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.68 | 19.36 | 20.04 | 20.72 | 21.4 | 22.16 | 22.92 | 23.68 | 24.44 | 25.2 | 26.28 | 27.36 | 28.44 | 29.52 | 30.6 | 31.88 | 33.16 | 34.44 | 35.72 | 37 | 38.44 | 39.88 | 41.32 | 42.76 | 44.2
18 | 1.2 | 18012 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.68 | 19.36 | 20.04 | 20.72 | 21.4 | 22.36 | 23.32 | 24.28 | 25.24 | 26.2 | 27.28 | 28.36 | 29.44 | 30.52 | 31.6 | 32.84 | 34.08 | 35.32 | 36.56 | 37.8 | 39.28 | 40.76 | 42.24 | 43.72 | 45.2
18 | 1.4 | 18014 | 15.6 | 16.16 | 16.72 | 17.28 | 17.84 | 18.4 | 19.08 | 19.76 | 20.44 | 21.12 | 21.8 | 22.68 | 23.56 | 24.44 | 25.32 | 26.2 | 27.36 | 28.52 | 29.68 | 30.84 | 32 | 33.36 | 34.72 | 36.08 | 37.44 | 38.8 | 40.36 | 41.92 | 43.48 | 45.04 | 46.6
18 | 1.6 | 18016 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.68 | 20.36 | 21.04 | 21.72 | 22.4 | 23.36 | 24.32 | 25.28 | 26.24 | 27.2 | 28.36 | 29.52 | 30.68 | 31.84 | 33 | 34.36 | 35.72 | 37.08 | 38.44 | 39.8 | 41.36 | 42.92 | 44.48 | 46.04 | 47.6
18 | 1.8 | 18018 | 16 | 16.68 | 17.36 | 18.04 | 18.72 | 19.4 | 20.08 | 20.76 | 21.44 | 22.12 | 22.8 | 23.88 | 24.96 | 26.04 | 27.12 | 28.2 | 29.36 | 30.52 | 31.68 | 32.84 | 34 | 35.36 | 36.72 | 38.08 | 39.44 | 40.8 | 42.44 | 44.08 | 45.72 | 47.36 | 49
18 | 2 | 18020 | 16.6 | 17.16 | 17.72 | 18.28 | 18.84 | 19.4 | 20.28 | 21.16 | 22.04 | 22.92 | 23.8 | 24.68 | 25.56 | 26.44 | 27.32 | 28.2 | 29.44 | 30.68 | 31.92 | 33.16 | 34.4 | 35.88 | 37.36 | 38.84 | 40.32 | 41.8 | 43.44 | 45.08 | 46.72 | 48.36 | 50
18 | 2.2 | 18022 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.76 | 21.52 | 22.28 | 23.04 | 23.8 | 24.88 | 25.96 | 27.04 | 28.12 | 29.2 | 30.36 | 31.52 | 32.68 | 33.84 | 35 | 36.56 | 38.12 | 39.68 | 41.24 | 42.8 | 44.44 | 46.08 | 47.72 | 49.36 | 51
18 | 2.4 | 18024 | 17 | 17.68 | 18.36 | 19.04 | 19.72 | 20.4 | 21.28 | 22.16 | 23.04 | 23.92 | 24.8 | 25.76 | 26.72 | 27.68 | 28.64 | 29.6 | 30.88 | 32.16 | 33.44 | 34.72 | 36 | 37.44 | 38.88 | 40.32 | 41.76 | 43.2 | 44.96 | 46.72 | 48.48 | 50.24 | 52
18 | 2.6 | 18026 | 17 | 17.68 | 18.36 | 19.04 | 19.72 | 20.4 | 21.28 | 22.16 | 23.04 | 23.92 | 24.8 | 25.96 | 27.12 | 28.28 | 29.44 | 30.6 | 31.76 | 32.92 | 34.08 | 35.24 | 36.4 | 37.96 | 39.52 | 41.08 | 42.64 | 44.2 | 46.04 | 47.88 | 49.72 | 51.56 | 53.4
18 | 2.8 | 18028 | 18 | 18.68 | 19.36 | 20.04 | 20.72 | 21.4 | 22.16 | 22.92 | 23.68 | 24.44 | 25.2 | 26.28 | 27.36 | 28.44 | 29.52 | 30.6 | 31.96 | 33.32 | 34.68 | 36.04 | 37.4 | 38.96 | 40.52 | 42.08 | 43.64 | 45.2 | 47.04 | 48.88 | 50.72 | 52.56 | 54.4
18 | 3 | 18030 | 18 | 18.68 | 19.36 | 20.04 | 20.72 | 21.4 | 22.28 | 23.16 | 24.04 | 24.92 | 25.8 | 26.96 | 28.12 | 29.28 | 30.44 | 31.6 | 32.96 | 34.32 | 35.68 | 37.04 | 38.4 | 39.96 | 41.52 | 43.08 | 44.64 | 46.2 | 48.04 | 49.88 | 51.72 | 53.56 | 55.4
19 | 0 | 19000 | 12.8 | 13.44 | 14.08 | 14.72 | 15.36 | 16 | 16.44 | 16.88 | 17.32 | 17.76 | 18.2 | 19.04 | 19.88 | 20.72 | 21.56 | 22.4 | 23.24 | 24.08 | 24.92 | 25.76 | 26.6 | 27.64 | 28.68 | 29.72 | 30.76 | 31.8 | 32.92 | 34.04 | 35.16 | 36.28 | 37.4
19 | 0.4 | 19004 | 12.8 | 13.44 | 14.08 | 14.72 | 15.36 | 16 | 16.44 | 16.88 | 17.32 | 17.76 | 18.2 | 19.04 | 19.88 | 20.72 | 21.56 | 22.4 | 23.24 | 24.08 | 24.92 | 25.76 | 26.6 | 27.64 | 28.68 | 29.72 | 30.76 | 31.8 | 32.92 | 34.04 | 35.16 | 36.28 | 37.4
19 | 0.6 | 19006 | 13.8 | 14.24 | 14.68 | 15.12 | 15.56 | 16 | 16.64 | 17.28 | 17.92 | 18.56 | 19.2 | 19.88 | 20.56 | 21.24 | 21.92 | 22.6 | 23.6 | 24.6 | 25.6 | 26.6 | 27.6 | 28.68 | 29.76 | 30.84 | 31.92 | 33 | 34.12 | 35.24 | 36.36 | 37.48 | 38.6
19 | 0.8 | 19008 | 13.8 | 14.24 | 14.68 | 15.12 | 15.56 | 16 | 16.64 | 17.28 | 17.92 | 18.56 | 19.2 | 20.04 | 20.88 | 21.72 | 22.56 | 23.4 | 24.28 | 25.16 | 26.04 | 26.92 | 27.8 | 29.04 | 30.28 | 31.52 | 32.76 | 34 | 35.28 | 36.56 | 37.84 | 39.12 | 40.4
19 | 1 | 19010 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.64 | 18.28 | 18.92 | 19.56 | 20.2 | 20.88 | 21.56 | 22.24 | 22.92 | 23.6 | 24.64 | 25.68 | 26.72 | 27.76 | 28.8 | 30.04 | 31.28 | 32.52 | 33.76 | 35 | 36.32 | 37.64 | 38.96 | 40.28 | 41.6
19 | 1.2 | 19012 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.64 | 18.28 | 18.92 | 19.56 | 20.2 | 21.08 | 21.96 | 22.84 | 23.72 | 24.6 | 25.64 | 26.68 | 27.72 | 28.76 | 29.8 | 30.92 | 32.04 | 33.16 | 34.28 | 35.4 | 36.84 | 38.28 | 39.72 | 41.16 | 42.6
19 | 1.4 | 19014 | 14.8 | 15.28 | 15.76 | 16.24 | 16.72 | 17.2 | 17.84 | 18.48 | 19.12 | 19.76 | 20.4 | 21.24 | 22.08 | 22.92 | 23.76 | 24.6 | 25.68 | 26.76 | 27.84 | 28.92 | 30 | 31.28 | 32.56 | 33.84 | 35.12 | 36.4 | 37.88 | 39.36 | 40.84 | 42.32 | 43.8
19 | 1.6 | 19016 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.64 | 19.28 | 19.92 | 20.56 | 21.2 | 22.08 | 22.96 | 23.84 | 24.72 | 25.6 | 26.68 | 27.76 | 28.84 | 29.92 | 31 | 32.28 | 33.56 | 34.84 | 36.12 | 37.4 | 38.88 | 40.36 | 41.84 | 43.32 | 44.8
19 | 1.8 | 19018 | 15 | 15.64 | 16.28 | 16.92 | 17.56 | 18.2 | 18.84 | 19.48 | 20.12 | 20.76 | 21.4 | 22.44 | 23.48 | 24.52 | 25.56 | 26.6 | 27.68 | 28.76 | 29.84 | 30.92 | 32 | 33.28 | 34.56 | 35.84 | 37.12 | 38.4 | 39.92 | 41.44 | 42.96 | 44.48 | 46
19 | 2 | 19020 | 15.8 | 16.28 | 16.76 | 17.24 | 17.72 | 18.2 | 19.04 | 19.88 | 20.72 | 21.56 | 22.4 | 23.24 | 24.08 | 24.92 | 25.76 | 26.6 | 27.72 | 28.84 | 29.96 | 31.08 | 32.2 | 33.64 | 35.08 | 36.52 | 37.96 | 39.4 | 40.92 | 42.44 | 43.96 | 45.48 | 47
19 | 2.2 | 19022 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.68 | 20.36 | 21.04 | 21.72 | 22.4 | 23.44 | 24.48 | 25.52 | 26.56 | 27.6 | 28.68 | 29.76 | 30.84 | 31.92 | 33 | 34.48 | 35.96 | 37.44 | 38.92 | 40.4 | 41.92 | 43.44 | 44.96 | 46.48 | 48
19 | 2.4 | 19024 | 16 | 16.64 | 17.28 | 17.92 | 18.56 | 19.2 | 20.04 | 20.88 | 21.72 | 22.56 | 23.4 | 24.28 | 25.16 | 26.04 | 26.92 | 27.8 | 29.04 | 30.28 | 31.52 | 32.76 | 34 | 35.32 | 36.64 | 37.96 | 39.28 | 40.6 | 42.28 | 43.96 | 45.64 | 47.32 | 49
19 | 2.6 | 19026 | 16 | 16.64 | 17.28 | 17.92 | 18.56 | 19.2 | 20.04 | 20.88 | 21.72 | 22.56 | 23.4 | 24.48 | 25.56 | 26.64 | 27.72 | 28.8 | 29.88 | 30.96 | 32.04 | 33.12 | 34.2 | 35.68 | 37.16 | 38.64 | 40.12 | 41.6 | 43.32 | 45.04 | 46.76 | 48.48 | 50.2
19 | 2.8 | 19028 | 17 | 17.64 | 18.28 | 18.92 | 19.56 | 20.2 | 20.88 | 21.56 | 22.24 | 22.92 | 23.6 | 24.64 | 25.68 | 26.72 | 27.76 | 28.8 | 30.08 | 31.36 | 32.64 | 33.92 | 35.2 | 36.68 | 38.16 | 39.64 | 41.12 | 42.6 | 44.32 | 46.04 | 47.76 | 49.48 | 51.2
19 | 3 | 19030 | 17 | 17.64 | 18.28 | 18.92 | 19.56 | 20.2 | 21.04 | 21.88 | 22.72 | 23.56 | 24.4 | 25.48 | 26.56 | 27.64 | 28.72 | 29.8 | 31.08 | 32.36 | 33.64 | 34.92 | 36.2 | 37.68 | 39.16 | 40.64 | 42.12 | 43.6 | 45.32 | 47.04 | 48.76 | 50.48 | 52.2
20 | 0 | 20000 | 12 | 12.6 | 13.2 | 13.8 | 14.4 | 15 | 15.4 | 15.8 | 16.2 | 16.6 | 17 | 17.8 | 18.6 | 19.4 | 20.2 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35
20 | 0.4 | 20004 | 12 | 12.6 | 13.2 | 13.8 | 14.4 | 15 | 15.4 | 15.8 | 16.2 | 16.6 | 17 | 17.8 | 18.6 | 19.4 | 20.2 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35
20 | 0.6 | 20006 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.6 | 19.2 | 19.8 | 20.4 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36
20 | 0.8 | 20008 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 22.8 | 23.6 | 24.4 | 25.2 | 26 | 27.2 | 28.4 | 29.6 | 30.8 | 32 | 33.2 | 34.4 | 35.6 | 36.8 | 38
20 | 1 | 20010 | 13 | 13.6 | 14.2 | 14.8 | 15.4 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.6 | 20.2 | 20.8 | 21.4 | 22 | 23 | 24 | 25 | 26 | 27 | 28.2 | 29.4 | 30.6 | 31.8 | 33 | 34.2 | 35.4 | 36.6 | 37.8 | 39
20 | 1.2 | 20012 | 13 | 13.6 | 14.2 | 14.8 | 15.4 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.8 | 20.6 | 21.4 | 22.2 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34.4 | 35.8 | 37.2 | 38.6 | 40
20 | 1.4 | 20014 | 14 | 14.4 | 14.8 | 15.2 | 15.6 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.8 | 20.6 | 21.4 | 22.2 | 23 | 24 | 25 | 26 | 27 | 28 | 29.2 | 30.4 | 31.6 | 32.8 | 34 | 35.4 | 36.8 | 38.2 | 39.6 | 41
20 | 1.6 | 20016 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.8 | 21.6 | 22.4 | 23.2 | 24 | 25 | 26 | 27 | 28 | 29 | 30.2 | 31.4 | 32.6 | 33.8 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42
20 | 1.8 | 20018 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31.2 | 32.4 | 33.6 | 34.8 | 36 | 37.4 | 38.8 | 40.2 | 41.6 | 43
20 | 2 | 20020 | 15 | 15.4 | 15.8 | 16.2 | 16.6 | 17 | 17.8 | 18.6 | 19.4 | 20.2 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26 | 27 | 28 | 29 | 30 | 31.4 | 32.8 | 34.2 | 35.6 | 37 | 38.4 | 39.8 | 41.2 | 42.6 | 44
20 | 2.2 | 20022 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.6 | 19.2 | 19.8 | 20.4 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32.4 | 33.8 | 35.2 | 36.6 | 38 | 39.4 | 40.8 | 42.2 | 43.6 | 45
20 | 2.4 | 20024 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 22.8 | 23.6 | 24.4 | 25.2 | 26 | 27.2 | 28.4 | 29.6 | 30.8 | 32 | 33.2 | 34.4 | 35.6 | 36.8 | 38 | 39.6 | 41.2 | 42.8 | 44.4 | 46
20 | 2.6 | 20026 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33.4 | 34.8 | 36.2 | 37.6 | 39 | 40.6 | 42.2 | 43.8 | 45.4 | 47
20 | 2.8 | 20028 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.6 | 20.2 | 20.8 | 21.4 | 22 | 23 | 24 | 25 | 26 | 27 | 28.2 | 29.4 | 30.6 | 31.8 | 33 | 34.4 | 35.8 | 37.2 | 38.6 | 40 | 41.6 | 43.2 | 44.8 | 46.4 | 48
20 | 3 | 20030 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.8 | 20.6 | 21.4 | 22.2 | 23 | 24 | 25 | 26 | 27 | 28 | 29.2 | 30.4 | 31.6 | 32.8 | 34 | 35.4 | 36.8 | 38.2 | 39.6 | 41 | 42.6 | 44.2 | 45.8 | 47.4 | 49
21 | 0 | 21000 | 11.2 | 11.76 | 12.32 | 12.88 | 13.44 | 14 | 14.4 | 14.8 | 15.2 | 15.6 | 16 | 16.72 | 17.44 | 18.16 | 18.88 | 19.6 | 20.36 | 21.12 | 21.88 | 22.64 | 23.4 | 24.32 | 25.24 | 26.16 | 27.08 | 28 | 28.92 | 29.84 | 30.76 | 31.68 | 32.6
21 | 0.4 | 21004 | 11.2 | 11.76 | 12.32 | 12.88 | 13.44 | 14 | 14.4 | 14.8 | 15.2 | 15.6 | 16 | 16.72 | 17.44 | 18.16 | 18.88 | 19.6 | 20.36 | 21.12 | 21.88 | 22.64 | 23.4 | 24.32 | 25.24 | 26.16 | 27.08 | 28 | 28.92 | 29.84 | 30.76 | 31.68 | 32.6
21 | 0.6 | 21006 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.36 | 17.92 | 18.48 | 19.04 | 19.6 | 20.52 | 21.44 | 22.36 | 23.28 | 24.2 | 25.12 | 26.04 | 26.96 | 27.88 | 28.8 | 29.76 | 30.72 | 31.68 | 32.64 | 33.6
21 | 0.8 | 21008 | 12.2 | 12.56 | 12.92 | 13.28 | 13.64 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.56 | 18.32 | 19.08 | 19.84 | 20.6 | 21.36 | 22.12 | 22.88 | 23.64 | 24.4 | 25.48 | 26.56 | 27.64 | 28.72 | 29.8 | 30.92 | 32.04 | 33.16 | 34.28 | 35.4
21 | 1 | 21010 | 12.2 | 12.72 | 13.24 | 13.76 | 14.28 | 14.8 | 15.36 | 15.92 | 16.48 | 17.04 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.6 | 21.52 | 22.44 | 23.36 | 24.28 | 25.2 | 26.32 | 27.44 | 28.56 | 29.68 | 30.8 | 31.92 | 33.04 | 34.16 | 35.28 | 36.4
21 | 1.2 | 21012 | 12.2 | 12.76 | 13.32 | 13.88 | 14.44 | 15 | 15.56 | 16.12 | 16.68 | 17.24 | 17.8 | 18.52 | 19.24 | 19.96 | 20.68 | 21.4 | 22.32 | 23.24 | 24.16 | 25.08 | 26 | 26.96 | 27.92 | 28.88 | 29.84 | 30.8 | 32.12 | 33.44 | 34.76 | 36.08 | 37.4
21 | 1.4 | 21014 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.56 | 16.12 | 16.68 | 17.24 | 17.8 | 18.56 | 19.32 | 20.08 | 20.84 | 21.6 | 22.52 | 23.44 | 24.36 | 25.28 | 26.2 | 27.32 | 28.44 | 29.56 | 30.68 | 31.8 | 33.08 | 34.36 | 35.64 | 36.92 | 38.2
21 | 1.6 | 21016 | 13 | 13.56 | 14.12 | 14.68 | 15.24 | 15.8 | 16.36 | 16.92 | 17.48 | 18.04 | 18.6 | 19.36 | 20.12 | 20.88 | 21.64 | 22.4 | 23.32 | 24.24 | 25.16 | 26.08 | 27 | 28.12 | 29.24 | 30.36 | 31.48 | 32.6 | 33.92 | 35.24 | 36.56 | 37.88 | 39.2
21 | 1.8 | 21018 | 13.2 | 13.72 | 14.24 | 14.76 | 15.28 | 15.8 | 16.4 | 17 | 17.6 | 18.2 | 18.8 | 19.68 | 20.56 | 21.44 | 22.32 | 23.2 | 24.16 | 25.12 | 26.08 | 27.04 | 28 | 29.12 | 30.24 | 31.36 | 32.48 | 33.6 | 34.92 | 36.24 | 37.56 | 38.88 | 40.2
21 | 2 | 21020 | 14 | 14.4 | 14.8 | 15.2 | 15.6 | 16 | 16.72 | 17.44 | 18.16 | 18.88 | 19.6 | 20.36 | 21.12 | 21.88 | 22.64 | 23.4 | 24.32 | 25.24 | 26.16 | 27.08 | 28 | 29.32 | 30.64 | 31.96 | 33.28 | 34.6 | 35.88 | 37.16 | 38.44 | 39.72 | 41
21 | 2.2 | 21022 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.36 | 17.92 | 18.48 | 19.04 | 19.6 | 20.52 | 21.44 | 22.36 | 23.28 | 24.2 | 25.16 | 26.12 | 27.08 | 28.04 | 29 | 30.28 | 31.56 | 32.84 | 34.12 | 35.4 | 36.72 | 38.04 | 39.36 | 40.68 | 42
21 | 2.4 | 21024 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.52 | 18.24 | 18.96 | 19.68 | 20.4 | 21.16 | 21.92 | 22.68 | 23.44 | 24.2 | 25.32 | 26.44 | 27.56 | 28.68 | 29.8 | 30.96 | 32.12 | 33.28 | 34.44 | 35.6 | 37.08 | 38.56 | 40.04 | 41.52 | 43
21 | 2.6 | 21026 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.56 | 18.32 | 19.08 | 19.84 | 20.6 | 21.52 | 22.44 | 23.36 | 24.28 | 25.2 | 26.16 | 27.12 | 28.08 | 29.04 | 30 | 31.28 | 32.56 | 33.84 | 35.12 | 36.4 | 37.88 | 39.36 | 40.84 | 42.32 | 43.8
21 | 2.8 | 21028 | 14.8 | 15.36 | 15.92 | 16.48 | 17.04 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.6 | 21.52 | 22.44 | 23.36 | 24.28 | 25.2 | 26.32 | 27.44 | 28.56 | 29.68 | 30.8 | 32.12 | 33.44 | 34.76 | 36.08 | 37.4 | 38.88 | 40.36 | 41.84 | 43.32 | 44.8
21 | 3 | 21030 | 15 | 15.56 | 16.12 | 16.68 | 17.24 | 17.8 | 18.52 | 19.24 | 19.96 | 20.68 | 21.4 | 22.32 | 23.24 | 24.16 | 25.08 | 26 | 27.12 | 28.24 | 29.36 | 30.48 | 31.6 | 32.92 | 34.24 | 35.56 | 36.88 | 38.2 | 39.68 | 41.16 | 42.64 | 44.12 | 45.6
22 | 0 | 22000 | 10.4 | 10.92 | 11.44 | 11.96 | 12.48 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.64 | 16.28 | 16.92 | 17.56 | 18.2 | 18.92 | 19.64 | 20.36 | 21.08 | 21.8 | 22.64 | 23.48 | 24.32 | 25.16 | 26 | 26.84 | 27.68 | 28.52 | 29.36 | 30.2
22 | 0.4 | 22004 | 10.4 | 10.92 | 11.44 | 11.96 | 12.48 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.64 | 16.28 | 16.92 | 17.56 | 18.2 | 18.92 | 19.64 | 20.36 | 21.08 | 21.8 | 22.64 | 23.48 | 24.32 | 25.16 | 26 | 26.84 | 27.68 | 28.52 | 29.36 | 30.2
22 | 0.6 | 22006 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.52 | 14.04 | 14.56 | 15.08 | 15.6 | 16.12 | 16.64 | 17.16 | 17.68 | 18.2 | 19.04 | 19.88 | 20.72 | 21.56 | 22.4 | 23.24 | 24.08 | 24.92 | 25.76 | 26.6 | 27.52 | 28.44 | 29.36 | 30.28 | 31.2
22 | 0.8 | 22008 | 11.4 | 11.72 | 12.04 | 12.36 | 12.68 | 13 | 13.52 | 14.04 | 14.56 | 15.08 | 15.6 | 16.32 | 17.04 | 17.76 | 18.48 | 19.2 | 19.92 | 20.64 | 21.36 | 22.08 | 22.8 | 23.76 | 24.72 | 25.68 | 26.64 | 27.6 | 28.64 | 29.68 | 30.72 | 31.76 | 32.8
22 | 1 | 22010 | 11.4 | 11.84 | 12.28 | 12.72 | 13.16 | 13.6 | 14.12 | 14.64 | 15.16 | 15.68 | 16.2 | 16.8 | 17.4 | 18 | 18.6 | 19.2 | 20.04 | 20.88 | 21.72 | 22.56 | 23.4 | 24.44 | 25.48 | 26.52 | 27.56 | 28.6 | 29.64 | 30.68 | 31.72 | 32.76 | 33.8
22 | 1.2 | 22012 | 11.4 | 11.92 | 12.44 | 12.96 | 13.48 | 14 | 14.52 | 15.04 | 15.56 | 16.08 | 16.6 | 17.24 | 17.88 | 18.52 | 19.16 | 19.8 | 20.64 | 21.48 | 22.32 | 23.16 | 24 | 24.92 | 25.84 | 26.76 | 27.68 | 28.6 | 29.84 | 31.08 | 32.32 | 33.56 | 34.8
22 | 1.4 | 22014 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.52 | 15.04 | 15.56 | 16.08 | 16.6 | 17.32 | 18.04 | 18.76 | 19.48 | 20.2 | 21.04 | 21.88 | 22.72 | 23.56 | 24.4 | 25.44 | 26.48 | 27.52 | 28.56 | 29.6 | 30.76 | 31.92 | 33.08 | 34.24 | 35.4
22 | 1.6 | 22016 | 12 | 12.52 | 13.04 | 13.56 | 14.08 | 14.6 | 15.12 | 15.64 | 16.16 | 16.68 | 17.2 | 17.92 | 18.64 | 19.36 | 20.08 | 20.8 | 21.64 | 22.48 | 23.32 | 24.16 | 25 | 26.04 | 27.08 | 28.12 | 29.16 | 30.2 | 31.44 | 32.68 | 33.92 | 35.16 | 36.4
22 | 1.8 | 22018 | 12.4 | 12.84 | 13.28 | 13.72 | 14.16 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.6 | 18.36 | 19.12 | 19.88 | 20.64 | 21.4 | 22.32 | 23.24 | 24.16 | 25.08 | 26 | 27.04 | 28.08 | 29.12 | 30.16 | 31.2 | 32.44 | 33.68 | 34.92 | 36.16 | 37.4
22 | 2 | 22020 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.64 | 16.28 | 16.92 | 17.56 | 18.2 | 18.92 | 19.64 | 20.36 | 21.08 | 21.8 | 22.64 | 23.48 | 24.32 | 25.16 | 26 | 27.24 | 28.48 | 29.72 | 30.96 | 32.2 | 33.36 | 34.52 | 35.68 | 36.84 | 38
22 | 2.2 | 22022 | 13 | 13.52 | 14.04 | 14.56 | 15.08 | 15.6 | 16.12 | 16.64 | 17.16 | 17.68 | 18.2 | 19.04 | 19.88 | 20.72 | 21.56 | 22.4 | 23.32 | 24.24 | 25.16 | 26.08 | 27 | 28.16 | 29.32 | 30.48 | 31.64 | 32.8 | 34.04 | 35.28 | 36.52 | 37.76 | 39
22 | 2.4 | 22024 | 13 | 13.52 | 14.04 | 14.56 | 15.08 | 15.6 | 16.24 | 16.88 | 17.52 | 18.16 | 18.8 | 19.52 | 20.24 | 20.96 | 21.68 | 22.4 | 23.44 | 24.48 | 25.52 | 26.56 | 27.6 | 28.72 | 29.84 | 30.96 | 32.08 | 33.2 | 34.56 | 35.92 | 37.28 | 38.64 | 40
22 | 2.6 | 22026 | 13 | 13.52 | 14.04 | 14.56 | 15.08 | 15.6 | 16.32 | 17.04 | 17.76 | 18.48 | 19.2 | 20.04 | 20.88 | 21.72 | 22.56 | 23.4 | 24.32 | 25.24 | 26.16 | 27.08 | 28 | 29.16 | 30.32 | 31.48 | 32.64 | 33.8 | 35.16 | 36.52 | 37.88 | 39.24 | 40.6
22 | 2.8 | 22028 | 13.6 | 14.12 | 14.64 | 15.16 | 15.68 | 16.2 | 16.8 | 17.4 | 18 | 18.6 | 19.2 | 20.04 | 20.88 | 21.72 | 22.56 | 23.4 | 24.44 | 25.48 | 26.52 | 27.56 | 28.6 | 29.84 | 31.08 | 32.32 | 33.56 | 34.8 | 36.16 | 37.52 | 38.88 | 40.24 | 41.6
22 | 3 | 22030 | 14 | 14.52 | 15.04 | 15.56 | 16.08 | 16.6 | 17.24 | 17.88 | 18.52 | 19.16 | 19.8 | 20.64 | 21.48 | 22.32 | 23.16 | 24 | 25.04 | 26.08 | 27.12 | 28.16 | 29.2 | 30.44 | 31.68 | 32.92 | 34.16 | 35.4 | 36.76 | 38.12 | 39.48 | 40.84 | 42.2
23 | 0 | 23000 | 9.6 | 10.08 | 10.56 | 11.04 | 11.52 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.48 | 18.16 | 18.84 | 19.52 | 20.2 | 20.96 | 21.72 | 22.48 | 23.24 | 24 | 24.76 | 25.52 | 26.28 | 27.04 | 27.8
23 | 0.4 | 23004 | 9.6 | 10.08 | 10.56 | 11.04 | 11.52 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.48 | 18.16 | 18.84 | 19.52 | 20.2 | 20.96 | 21.72 | 22.48 | 23.24 | 24 | 24.76 | 25.52 | 26.28 | 27.04 | 27.8
23 | 0.6 | 23006 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.48 | 12.96 | 13.44 | 13.92 | 14.4 | 14.88 | 15.36 | 15.84 | 16.32 | 16.8 | 17.56 | 18.32 | 19.08 | 19.84 | 20.6 | 21.36 | 22.12 | 22.88 | 23.64 | 24.4 | 25.28 | 26.16 | 27.04 | 27.92 | 28.8
23 | 0.8 | 23008 | 10.6 | 10.88 | 11.16 | 11.44 | 11.72 | 12 | 12.48 | 12.96 | 13.44 | 13.92 | 14.4 | 15.08 | 15.76 | 16.44 | 17.12 | 17.8 | 18.48 | 19.16 | 19.84 | 20.52 | 21.2 | 22.04 | 22.88 | 23.72 | 24.56 | 25.4 | 26.36 | 27.32 | 28.28 | 29.24 | 30.2
23 | 1 | 23010 | 10.6 | 10.96 | 11.32 | 11.68 | 12.04 | 12.4 | 12.88 | 13.36 | 13.84 | 14.32 | 14.8 | 15.4 | 16 | 16.6 | 17.2 | 17.8 | 18.56 | 19.32 | 20.08 | 20.84 | 21.6 | 22.56 | 23.52 | 24.48 | 25.44 | 26.4 | 27.36 | 28.32 | 29.28 | 30.24 | 31.2
23 | 1.2 | 23012 | 10.6 | 11.08 | 11.56 | 12.04 | 12.52 | 13 | 13.48 | 13.96 | 14.44 | 14.92 | 15.4 | 15.96 | 16.52 | 17.08 | 17.64 | 18.2 | 18.96 | 19.72 | 20.48 | 21.24 | 22 | 22.88 | 23.76 | 24.64 | 25.52 | 26.4 | 27.56 | 28.72 | 29.88 | 31.04 | 32.2
23 | 1.4 | 23014 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.48 | 13.96 | 14.44 | 14.92 | 15.4 | 16.08 | 16.76 | 17.44 | 18.12 | 18.8 | 19.56 | 20.32 | 21.08 | 21.84 | 22.6 | 23.56 | 24.52 | 25.48 | 26.44 | 27.4 | 28.44 | 29.48 | 30.52 | 31.56 | 32.6
23 | 1.6 | 23016 | 11 | 11.48 | 11.96 | 12.44 | 12.92 | 13.4 | 13.88 | 14.36 | 14.84 | 15.32 | 15.8 | 16.48 | 17.16 | 17.84 | 18.52 | 19.2 | 19.96 | 20.72 | 21.48 | 22.24 | 23 | 23.96 | 24.92 | 25.88 | 26.84 | 27.8 | 28.96 | 30.12 | 31.28 | 32.44 | 33.6
23 | 1.8 | 23018 | 11.6 | 11.96 | 12.32 | 12.68 | 13.04 | 13.4 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17.04 | 17.68 | 18.32 | 18.96 | 19.6 | 20.48 | 21.36 | 22.24 | 23.12 | 24 | 24.96 | 25.92 | 26.88 | 27.84 | 28.8 | 29.96 | 31.12 | 32.28 | 33.44 | 34.6
23 | 2 | 23020 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.56 | 15.12 | 15.68 | 16.24 | 16.8 | 17.48 | 18.16 | 18.84 | 19.52 | 20.2 | 20.96 | 21.72 | 22.48 | 23.24 | 24 | 25.16 | 26.32 | 27.48 | 28.64 | 29.8 | 30.84 | 31.88 | 32.92 | 33.96 | 35
23 | 2.2 | 23022 | 12 | 12.48 | 12.96 | 13.44 | 13.92 | 14.4 | 14.88 | 15.36 | 15.84 | 16.32 | 16.8 | 17.56 | 18.32 | 19.08 | 19.84 | 20.6 | 21.48 | 22.36 | 23.24 | 24.12 | 25 | 26.04 | 27.08 | 28.12 | 29.16 | 30.2 | 31.36 | 32.52 | 33.68 | 34.84 | 36
23 | 2.4 | 23024 | 12 | 12.48 | 12.96 | 13.44 | 13.92 | 14.4 | 14.96 | 15.52 | 16.08 | 16.64 | 17.2 | 17.88 | 18.56 | 19.24 | 19.92 | 20.6 | 21.56 | 22.52 | 23.48 | 24.44 | 25.4 | 26.48 | 27.56 | 28.64 | 29.72 | 30.8 | 32.04 | 33.28 | 34.52 | 35.76 | 37
23 | 2.6 | 23026 | 12 | 12.48 | 12.96 | 13.44 | 13.92 | 14.4 | 15.08 | 15.76 | 16.44 | 17.12 | 17.8 | 18.56 | 19.32 | 20.08 | 20.84 | 21.6 | 22.48 | 23.36 | 24.24 | 25.12 | 26 | 27.04 | 28.08 | 29.12 | 30.16 | 31.2 | 32.44 | 33.68 | 34.92 | 36.16 | 37.4
23 | 2.8 | 23028 | 12.4 | 12.88 | 13.36 | 13.84 | 14.32 | 14.8 | 15.4 | 16 | 16.6 | 17.2 | 17.8 | 18.56 | 19.32 | 20.08 | 20.84 | 21.6 | 22.56 | 23.52 | 24.48 | 25.44 | 26.4 | 27.56 | 28.72 | 29.88 | 31.04 | 32.2 | 33.44 | 34.68 | 35.92 | 37.16 | 38.4
23 | 3 | 23030 | 13 | 13.48 | 13.96 | 14.44 | 14.92 | 15.4 | 15.96 | 16.52 | 17.08 | 17.64 | 18.2 | 18.96 | 19.72 | 20.48 | 21.24 | 22 | 22.96 | 23.92 | 24.88 | 25.84 | 26.8 | 27.96 | 29.12 | 30.28 | 31.44 | 32.6 | 33.84 | 35.08 | 36.32 | 37.56 | 38.8
24 | 0 | 24000 | 8.8 | 9.24 | 9.68 | 10.12 | 10.56 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.48 | 13.96 | 14.44 | 14.92 | 15.4 | 16.04 | 16.68 | 17.32 | 17.96 | 18.6 | 19.28 | 19.96 | 20.64 | 21.32 | 22 | 22.68 | 23.36 | 24.04 | 24.72 | 25.4
24 | 0.4 | 24004 | 8.8 | 9.24 | 9.68 | 10.12 | 10.56 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.48 | 13.96 | 14.44 | 14.92 | 15.4 | 16.04 | 16.68 | 17.32 | 17.96 | 18.6 | 19.28 | 19.96 | 20.64 | 21.32 | 22 | 22.68 | 23.36 | 24.04 | 24.72 | 25.4
24 | 0.6 | 24006 | 9 | 9.4 | 9.8 | 10.2 | 10.6 | 11 | 11.44 | 11.88 | 12.32 | 12.76 | 13.2 | 13.64 | 14.08 | 14.52 | 14.96 | 15.4 | 16.08 | 16.76 | 17.44 | 18.12 | 18.8 | 19.48 | 20.16 | 20.84 | 21.52 | 22.2 | 23.04 | 23.88 | 24.72 | 25.56 | 26.4
24 | 0.8 | 24008 | 9.8 | 10.04 | 10.28 | 10.52 | 10.76 | 11 | 11.44 | 11.88 | 12.32 | 12.76 | 13.2 | 13.84 | 14.48 | 15.12 | 15.76 | 16.4 | 17.04 | 17.68 | 18.32 | 18.96 | 19.6 | 20.32 | 21.04 | 21.76 | 22.48 | 23.2 | 24.08 | 24.96 | 25.84 | 26.72 | 27.6
24 | 1 | 24010 | 9.8 | 10.08 | 10.36 | 10.64 | 10.92 | 11.2 | 11.64 | 12.08 | 12.52 | 12.96 | 13.4 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17.08 | 17.76 | 18.44 | 19.12 | 19.8 | 20.68 | 21.56 | 22.44 | 23.32 | 24.2 | 25.08 | 25.96 | 26.84 | 27.72 | 28.6
24 | 1.2 | 24012 | 9.8 | 10.24 | 10.68 | 11.12 | 11.56 | 12 | 12.44 | 12.88 | 13.32 | 13.76 | 14.2 | 14.68 | 15.16 | 15.64 | 16.12 | 16.6 | 17.28 | 17.96 | 18.64 | 19.32 | 20 | 20.84 | 21.68 | 22.52 | 23.36 | 24.2 | 25.28 | 26.36 | 27.44 | 28.52 | 29.6
24 | 1.4 | 24014 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.44 | 12.88 | 13.32 | 13.76 | 14.2 | 14.84 | 15.48 | 16.12 | 16.76 | 17.4 | 18.08 | 18.76 | 19.44 | 20.12 | 20.8 | 21.68 | 22.56 | 23.44 | 24.32 | 25.2 | 26.12 | 27.04 | 27.96 | 28.88 | 29.8
24 | 1.6 | 24016 | 10 | 10.44 | 10.88 | 11.32 | 11.76 | 12.2 | 12.64 | 13.08 | 13.52 | 13.96 | 14.4 | 15.04 | 15.68 | 16.32 | 16.96 | 17.6 | 18.28 | 18.96 | 19.64 | 20.32 | 21 | 21.88 | 22.76 | 23.64 | 24.52 | 25.4 | 26.48 | 27.56 | 28.64 | 29.72 | 30.8
24 | 1.8 | 24018 | 10.8 | 11.08 | 11.36 | 11.64 | 11.92 | 12.2 | 12.8 | 13.4 | 14 | 14.6 | 15.2 | 15.72 | 16.24 | 16.76 | 17.28 | 17.8 | 18.64 | 19.48 | 20.32 | 21.16 | 22 | 22.88 | 23.76 | 24.64 | 25.52 | 26.4 | 27.48 | 28.56 | 29.64 | 30.72 | 31.8
24 | 2 | 24020 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.48 | 13.96 | 14.44 | 14.92 | 15.4 | 16.04 | 16.68 | 17.32 | 17.96 | 18.6 | 19.28 | 19.96 | 20.64 | 21.32 | 22 | 23.08 | 24.16 | 25.24 | 26.32 | 27.4 | 28.32 | 29.24 | 30.16 | 31.08 | 32
24 | 2.2 | 24022 | 11 | 11.44 | 11.88 | 12.32 | 12.76 | 13.2 | 13.64 | 14.08 | 14.52 | 14.96 | 15.4 | 16.08 | 16.76 | 17.44 | 18.12 | 18.8 | 19.64 | 20.48 | 21.32 | 22.16 | 23 | 23.92 | 24.84 | 25.76 | 26.68 | 27.6 | 28.68 | 29.76 | 30.84 | 31.92 | 33
24 | 2.4 | 24024 | 11 | 11.44 | 11.88 | 12.32 | 12.76 | 13.2 | 13.68 | 14.16 | 14.64 | 15.12 | 15.6 | 16.24 | 16.88 | 17.52 | 18.16 | 18.8 | 19.68 | 20.56 | 21.44 | 22.32 | 23.2 | 24.24 | 25.28 | 26.32 | 27.36 | 28.4 | 29.52 | 30.64 | 31.76 | 32.88 | 34
24 | 2.6 | 24026 | 11 | 11.44 | 11.88 | 12.32 | 12.76 | 13.2 | 13.84 | 14.48 | 15.12 | 15.76 | 16.4 | 17.08 | 17.76 | 18.44 | 19.12 | 19.8 | 20.64 | 21.48 | 22.32 | 23.16 | 24 | 24.92 | 25.84 | 26.76 | 27.68 | 28.6 | 29.72 | 30.84 | 31.96 | 33.08 | 34.2
24 | 2.8 | 24028 | 11.2 | 11.64 | 12.08 | 12.52 | 12.96 | 13.4 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17.08 | 17.76 | 18.44 | 19.12 | 19.8 | 20.68 | 21.56 | 22.44 | 23.32 | 24.2 | 25.28 | 26.36 | 27.44 | 28.52 | 29.6 | 30.72 | 31.84 | 32.96 | 34.08 | 35.2
24 | 3 | 24030 | 12 | 12.44 | 12.88 | 13.32 | 13.76 | 14.2 | 14.68 | 15.16 | 15.64 | 16.12 | 16.6 | 17.28 | 17.96 | 18.64 | 19.32 | 20 | 20.88 | 21.76 | 22.64 | 23.52 | 24.4 | 25.48 | 26.56 | 27.64 | 28.72 | 29.8 | 30.92 | 32.04 | 33.16 | 34.28 | 35.4
25 | 0 | 25000 | 8 | 8.4 | 8.8 | 9.2 | 9.6 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.6 | 21.2 | 21.8 | 22.4 | 23
25 | 0.4 | 25004 | 8 | 8.4 | 8.8 | 9.2 | 9.6 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.6 | 21.2 | 21.8 | 22.4 | 23
25 | 0.6 | 25006 | 8 | 8.4 | 8.8 | 9.2 | 9.6 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 20.8 | 21.6 | 22.4 | 23.2 | 24
25 | 0.8 | 25008 | 9 | 9.2 | 9.4 | 9.6 | 9.8 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.6 | 13.2 | 13.8 | 14.4 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.6 | 19.2 | 19.8 | 20.4 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25
25 | 1 | 25010 | 9 | 9.2 | 9.4 | 9.6 | 9.8 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.6 | 13.2 | 13.8 | 14.4 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 22.8 | 23.6 | 24.4 | 25.2 | 26
25 | 1.2 | 25012 | 9 | 9.4 | 9.8 | 10.2 | 10.6 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 23 | 24 | 25 | 26 | 27
25 | 1.4 | 25014 | 9 | 9.4 | 9.8 | 10.2 | 10.6 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.6 | 14.2 | 14.8 | 15.4 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.8 | 20.6 | 21.4 | 22.2 | 23 | 23.8 | 24.6 | 25.4 | 26.2 | 27
25 | 1.6 | 25016 | 9 | 9.4 | 9.8 | 10.2 | 10.6 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.6 | 14.2 | 14.8 | 15.4 | 16 | 16.6 | 17.2 | 17.8 | 18.4 | 19 | 19.8 | 20.6 | 21.4 | 22.2 | 23 | 24 | 25 | 26 | 27 | 28
25 | 1.8 | 25018 | 10 | 10.2 | 10.4 | 10.6 | 10.8 | 11 | 11.6 | 12.2 | 12.8 | 13.4 | 14 | 14.4 | 14.8 | 15.2 | 15.6 | 16 | 16.8 | 17.6 | 18.4 | 19.2 | 20 | 20.8 | 21.6 | 22.4 | 23.2 | 24 | 25 | 26 | 27 | 28 | 29
25 | 2 | 25020 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.6 | 18.2 | 18.8 | 19.4 | 20 | 21 | 22 | 23 | 24 | 25 | 25.8 | 26.6 | 27.4 | 28.2 | 29
25 | 2.2 | 25022 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.8 | 18.6 | 19.4 | 20.2 | 21 | 21.8 | 22.6 | 23.4 | 24.2 | 25 | 26 | 27 | 28 | 29 | 30
25 | 2.4 | 25024 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.6 | 15.2 | 15.8 | 16.4 | 17 | 17.8 | 18.6 | 19.4 | 20.2 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
25 | 2.6 | 25026 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.6 | 13.2 | 13.8 | 14.4 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 22.8 | 23.6 | 24.4 | 25.2 | 26 | 27 | 28 | 29 | 30 | 31
25 | 2.8 | 25028 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.6 | 13.2 | 13.8 | 14.4 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32
25 | 3 | 25030 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.4 | 13.8 | 14.2 | 14.6 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.8 | 19.6 | 20.4 | 21.2 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32
Notes:
| 1. |  | 6: Table values were obtained by linear interpolation using CT values published in USEPA's Guidance Manual for Compliance with the Filtration and Disinfection
Requirements for Public Water Systems Using Surface Water Sources, March 1991 edition. This table was developed by Nancy Feagin, P.E. of the
Drinking Water Northwest Regional Office
| 2. |  | 6: For other levels of log inactivation, multiply the table values by the log inactivation required. For example, for 0.5 log inactivation multiply the table values by 0.5.
| 3. |  | 6: For systems with pH values exceeding 9.0 see the Interim Enhanced Surface Water Treatment Rule Notice of Data Availability, Federal Register, November 3, 1997.