## WData (hidden)
2007-07-17 13:37
TRUE
2007-07-17 13:37
6:00

## Instructions
Instructions for filling out the OPS Water Wizard.
OPS will create the variables for your database (facility) from these sheets. Create/Edit a sheet for each location/sampling point in your plant.
Delete Rows for variables that are not tracked at your site. You can create as many rows in a sheet as you like.
Creating or Copying sheets
To create a new location/sheet simply right click on the sheet tab (at the bottom of the workbook) and click copy.
For example, after you have edited Filter 1 with all the variables and settings you want, right click on the Filter 1 tab
at the bottom, go to Move or Copy, check the Create a copy option and choose where you want it to go in the list
Deleting sheets not used
You may need to delete a sheet (I.e. you do not have a ClearWell so you need to get rid of that sheet).
Simply right click on the Clearwell tab and choose delete.
Give us a call at 800-677-0067 if you have any questions or need help getting started.
DO NOT ADD COLUMNS OR REARRANGE COLUMNS AS WE WILL NOT BE ABLE TO CREATE A DATABASE IF THE COLUMNS ARE CHANGED

## Plant
Location: | Plant | Area Name: |  |  | Desc
Location Name | Plant
Short Location Name | Plant
Desc: | General Plant/Weather
Base Var # | 100
Interface Settings
| Parameter | Short |  |  |  | Dec | Allow |  | Entry Min | Entry Max | Description | Storet |  |  | Low | High | Scale
Var # | Name | Name | Frequency | Type | Units | Plcs | Symbol | Equation |  |  | (Notes) | Code | Signal Tag | Statistic | Range | Range | Factor
1 | Time | Time | Daily | Text Parameter | Time |  | FALSE
11 | Wind Speed | Wind Spd | Daily | Parameter | MPH | 1 | FALSE
15 | Wind Direction | Wind Dir | Daily | Parameter | Deg | 0 | FALSE
21 | Rainfall | Rain | Daily | Parameter | Inches | 1 | FALSE |  |  | 2
31 | Temperature | Temp | Daily | Parameter | Deg F | 1 | FALSE |  | -10 | 110
41 | Weather description | Weather | Daily | Text Parameter |  | 0 | FALSE
51 | Operator on Duty | Operator | Day | Parameter | Initials | 0 | FALSE
61 | Hours of Operation | Hours | Day | Parameter | Hours | 1 | FALSE
Note on C7: Scott Dorner: Location and Parameter Name will create the variable name (up to 40 characters)
Note on D7: 20 Characters Max, combined with Short (C2)
Note on E7: Select from: OPS 32 Day Hour 15 Minute OPS SQL Day 4 Hours Hour 30 Minutes 15 Minutes 5 Minutes Minute
Note on F7: Select From: Parameter Text Parameter Calculated
Note on G7: 10 Characters Max
Note on H7: 0 will be used if left blank
Note on I7: Set to 1, TRUE, or Y if the Parameter should allow data qualifiers (<,>, or ND)
Note on P7: Select from: Min Max Total Avg First Last Start Value End Value
Note on Q7: Interface. Enter minimum value to use as filter. Ie if 0 is entered, values<0 will be ignored when importing data.
Note on R7: Ie if 9999 is entered, values>9999 will be ignored when importing data.
Note on S7: Enter a value by which the imported data will be multiplied to convert it to the proper units. Leave it blank if no change is necessary.
Note on B2: Combined with Parameter Name to make Variable Name
Note on B3: Combined with Short Name to make Heading
Note on K7: Entry Min and Max sets warning limits when entering data for the variable. When entering data, if a value is entered outside of the range a warning message will be displayed and the user will be asked if they want to keep or discard the entry.

## Raw
Location: | Raw | Area Name:
Location Name | Raw
Short Location Name | Raw
Desc: | Raw Water Influent
Base Var # | 1000
| Parameter | Short |  |  |  | Dec | Allow |  | Entry | Entry | Description | Storet |  |  | Low | High | Scale
Var # | Name | Name | Frequency | Type | Units | Plcs | Symbol | Equation | Min | max | (Notes) | Code | Scada Tag | Statistic | Range | Range | Factor
1 | Flow | Flow | Day | Parameter | MGD | 3 | FALSE |  |  |  |  | 50050 |  | Avg
2 | Flow | Flow | Day | Parameter | gpm | 1 | FALSE |  |  |  |  | 00058 |  | Avg
11 | Total Suspended Solids | TSS | Day | Parameter | mg/L | 0 | FALSE |  |  |  |  | 00530 |  | Avg
21 | Hardness (CaCO3) | Hard | Day | Parameter | mg/L | 0 | FALSE |  |  |  |  | 00900 |  | Avg
31 | Alkalinity (CaCO3) | Alkal | Day | Parameter | mg/L | 2 | FALSE |  |  |  |  | 00410 |  | Avg
35 | Total Organic Carbon | TOC | Day | Parameter | mg/L | 2 | FALSE |  |  |  |  | 03726
41 | Turbidity 15 Min | Turb | 15 Minute | Parameter | NTU | 2 | FALSE |  |  |  |  | 82078 |  | Avg
42 | Turbidity | Turb | Day | Parameter | NTU | 2 | FALSE |  |  |  |  | 82078 |  | Avg
43 | Turbidity Hrly | Turb | Hour | Parameter | NTU | 2 | FALSE |  |  |  |  | 82078 |  | Avg
51 | Dissolved Oxygen | DO | Day | Parameter | mg/L | 2 | TRUE |  |  |  |  | 00300 |  | Avg
61 | Carbon Dioxide | CO2 | Day | Parameter | mg/L | 2 | TRUE |  |  |  |  | 00405 |  | Avg
71 | Aluminum | Al | Day | Parameter | ug/L | 2 | TRUE |  |  |  |  | 01105 |  | Avg
81 | Arsenic | As | Day | Parameter | ug/L | 0 | TRUE |  |  |  |  | 01002 |  | Avg
91 | Chloride | Cl | Day | Parameter | mg/L | 2 | TRUE |  |  |  |  | 00940 |  | Avg
101 | Chlorine Residual Max | Cl2 Max | Day | Parameter | mg/L | 2 | FALSE |  |  |  |  | 50060 |  | Max
102 | Chlorine Residual Min | Cl2 Min | Day | Parameter | mg/L | 2 | FALSE |  |  |  |  | 50060 |  | Min
103 | Chlorine Residual Avg | Cl2 Avg | Day | Parameter | mg/L | 2 | FALSE |  |  |  |  | 50060 |  | Avg
111 | Color | Color | Day | Parameter | ColorUnits | 0 | FALSE |  |  |  |  | 00079 |  | Avg
121 | Copper | Cu | Day | Parameter | ug/L | 0 | TRUE |  |  |  |  | 01042 |  | Avg
131 | Corrosivity | Corros | Day | Parameter | WtrNum | 0 | FALSE |  |  |  |  | 71814 |  | Avg
141 | Fluoride | F- | Day | Parameter | mg/L | 3 | TRUE |  |  |  |  | 00951 |  | Avg
151 | Foaming Agents | Foam | Day | Parameter | mg/L | 2 | FALSE |  |  |  |  | 01288 |  | Avg
161 | Iron | Fe | Day | Parameter | ug/L | 0 | TRUE |  |  |  |  | 01045 |  | Avg
171 | Lead | Pb | Day | Parameter | ug/L | 0 | TRUE |  |  |  |  | 01051 |  | Avg
181 | Manganese | Mn | Day | Parameter | ug/L | 0 | TRUE |  |  |  |  | 01055 |  | Avg
191 | Nitrate/Nitrite | NO 3/2 | Day | Parameter | ug/L | 2 | TRUE |  |  |  |  | 00630 |  | Avg
201 | Odor | Odor | Day | Parameter | Code | 0 | FALSE |  |  |  |  | 34773 |  | Avg
211 | Silver | Ag | Day | Parameter | ug/L | 0 | TRUE |  |  |  |  | 01077 |  | Avg
221 | Sulfate | SO4 | Day | Parameter | mg/L | 3 | TRUE |  |  |  |  | 00945 |  | Avg
231 | Total Dissolved Solids | TDS | Day | Parameter | mg/L | 2 | TRUE |  |  |  |  | 47004 |  | Avg
241 | Zinc | Zn | Day | Parameter | ug/L | 0 | TRUE |  |  |  |  | 01092 |  | Avg
251 | pH | pH | Day | Parameter | SU | 1 | FALSE |  |  |  |  | 00400 |  | Avg
261 | Temperature | Temp | Day | Parameter | Deg F | 0 | FALSE |  |  |  |  | 00011 |  | Avg
271 | Temperature | Temp | Day | Parameter | Deg C | 0 | FALSE |  |  |  |  | 00010 |  | Avg
281 | Run Time | Run Time | Day | Parameter | hrs | 1 | FALSE | [6 empty] | Avg
291 | Pumping Level | Pump Lvl | Day | Parameter | ft | 1 | FALSE | [6 empty] | Avg
301 | Static Level | Static Lvl | Day | Parameter | ft | 1 | FALSE | [6 empty] | Avg
311 | Hours at Rest | Hrs Rest | Day | Parameter | hrs | 2 | FALSE | [6 empty] | Avg
321 | Zeta Potential | Zeta | Day | Parameter | mV | 0 | FALSE | [6 empty] | Avg
331 | Power | Pwr | Day | Parameter | kwH | 2 | FALSE | [6 empty] | Avg
341 | Average Level | AvgLvl | Day | Parameter | ft | 1 | FALSE | [6 empty] | Avg
351 | Minimum Level | MinLvl | Day | Parameter | ft | 1 | FALSE | [6 empty] | Avg
361 | Maximum Level | MaxLvl | Day | Parameter | ft | 1 | FALSE | [6 empty] | Avg
371 | Average Pressure | AvgPress | Day | Parameter | psi | 0 | FALSE | [6 empty] | Avg
381 | Minimum Pressure | MinPress | Day | Parameter | psi | 0 | FALSE | [6 empty] | Avg
391 | Maximum Pressure | MaxPress | Day | Parameter | psi | 0 | FALSE | [6 empty] | Avg
401 | Alum | Alum | Day | Parameter | #/day | 1 | FALSE | [6 empty] | Avg
411 | Alum | Alum | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
421 | Alum Dose | AlumDose | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
431 | Polymer | Poly | Day | Parameter | #/day | 1 | FALSE | [6 empty] | Avg
441 | Polymer | Poly | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
451 | Polymer Dose | PolyDose | Day | Parameter | mg/L | 0 | FALSE | [6 empty] | Avg
461 | Ferric Chloride | FeCl3 | Day | Parameter | #/day | 1 | FALSE | [6 empty] | Avg
471 | Ferric Chloride | FeCl3 | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
481 | Ferric Chloride Dose | FeCl3Dose | Day | Parameter | mg/L | 0 | FALSE | [6 empty] | Avg
491 | Potassium Permanganate | KmnO4 | Day | Parameter | #/day | 1 | FALSE | [6 empty] | Avg
501 | Potassium Permanganate | KmnO4 | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
511 | Potassium Permanganate Dose | KmnO4Dose | Day | Parameter | mg/L | 0 | FALSE | [6 empty] | Avg
521 | Chlorine | Cl2 | Day | Parameter | #/day | 1 | FALSE | [6 empty] | Avg
531 | Chlorine Dose | Cl2Dose | Day | Parameter | mg/L | 0 | FALSE | [6 empty] | Avg
541 | Sodium hypochlorite | NaOCl | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
551 | Sodium hypochlorite | NaOClDose | Day | Parameter | mg/L | 0 | FALSE | [6 empty] | Avg
561 | Hydrofluoric acid | HF | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
571 | Hydrofluoric acid Dose | HF Dose | Day | Parameter | mg/L | 0 | FALSE | [6 empty] | Avg
581 | Sodium hydroxide | NaOH | Day | Parameter | #/day | 1 | FALSE | [6 empty] | Avg
591 | Sodium hydroxide Dose | NaOH Dose | Day | Parameter | mg/L | 0 | FALSE | [6 empty] | Avg
601 | Polyphosphates | PolyP | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
611 | Polyphosphates Dose | PolyPDose | Day | Parameter | mg/L | 0 | FALSE | [6 empty] | Avg
621 | Fluorosilicic acid | H2SiF4 | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
631 | Fluorosilicic acid Dose | H2SiF4Ds | Day | Parameter | mg/L | 0 | FALSE | [6 empty] | Avg
641 | Surface Loading Rate | SurfLdg | Day | Parameter | gpd/ft2 | 2 | FALSE | [6 empty] | Avg
651 | Operator on Duty | Operator | Day | Parameter | Initials | 0 | FALSE | [6 empty] | Avg
661 | # of Backwashes | # BW | Day | Parameter | Count | 0 | FALSE | [6 empty] | Avg
671 | Status | Status | Hour | Parameter | Status | 0 | FALSE | [6 empty] | Avg
681 | RunTime at Backwash | RT @ BW | Day | Parameter | Hours | 1 | FALSE | [6 empty] | Avg
691 | RunTime Since Backwash | RT Since BW | Day | Parameter | Hours | 1 | FALSE | [6 empty] | Avg
801 | Segment Volume | Vol | Day | Calculated | MG | 1 | FALSE
811 | T10 | T10 | Day | Calculated | Mins | 1 | FALSE | ((Segment Vol (MG) / Flow (MGD) ) *24 * 60) * Baffling Factor
821 | CT Achieved | CT Achvd | Day | Calculated | mg/L - mins | 1 | FALSE | CL2 Residual (mg/L) * T10 (mins)
831 | 3 Log Giardia CT Required | 3L CT Req | Day | Calculated | mg/L - mins | 1 | FALSE | Final Temperature, pH, CL2
841 | 4 Log Viruses CT Required | 4 Log CT Req | Day | Calculated | mg/L - mins | 1 | FALSE | Table for Inactivation of viruses
851 | 3 Log Giardia CT Ratio | 3 Log CT Ratio | Day | Calculated | Ratio | 1 | FALSE | CT Achieved / 3 Log Giardia CT Required
861 | 4 Log Viruses CT Ratio | 4 Log CT Ratio | Day | Calculated | Ratio | 1 | FALSE | CT Achieved / 4 Log CT Required
871 | Giardia Log Inactivation | Gia Inact | Day | Calculated | Units | 1 | FALSE | 3 * 3 Log Giardia CT Ratio
881 | Viruses Log Inactivation |  | Day | Calculated | Units | 1 | FALSE | 3 * 4 Log Viruses Ratio
Note on E7: Select from: Day 4 Hours Hour 30 Minutes 15 Minutes 5 Minutes Minute
Note on F7: Select From: Parameter Text Parameter Calculated
Note on H7: 0 will be used if left blank
Note on P7: Select from: Min Max Total Avg First Last Start Value End Value
Note on Q7: Interface. Enter minimum value to use as filter. Ie if 0 is entered, values<0 will be ignored when importing data.
Note on R7: Ie if 9999 is entered, values>9999 will be ignored when importing data.
Note on S7: Enter a value by which the imported data will be multiplied to convert it to the proper units. Leave it blank if no change is necessary.
Note on I7: Set to 1, TRUE, or Y if the Parameter should allow data qualifiers (<,>, or ND)
Note on C7: Scott Dorner: Location and Parameter Name will create the variable name (up to 40 characters)
Note on G7: 10 Characters Max
Note on D7: 20 Characters Max, combined with Short (C2)
Note on B2: Combined with Parameter Name to make Variable Name
Note on B3: Combined with Short Name to make Heading

## Flash Mix
Location: | Flash Mix | Area Name:
Location Name | FlshMix
Short Location Name | Fmix
Desc: | Flash Mix/ Chem Addition
Base Var # | 2000
| Parameter | Short |  |  |  | Dec | Allow |  | Entry | Entry | Description | Storet |  |  | Low | High | Scale
Var # | Name | Name | Frequency | Type | Units | Plcs | Symbol | Equation | Min | max | (Notes) | Code | Scada Tag | Statistic | Range | Range | Factor
1 | Alum | Alum | Day | Parameter | #/day | 1 | FALSE | [6 empty] | Avg
11 | Alum | Alum | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
21 | Alum Dose | Alum Dose | Day | Parameter | mg/L | 0 | FALSE | [6 empty] | Avg
31 | Polymer | Poly | Day | Parameter | #/day | 1 | FALSE | [6 empty] | Avg
41 | Polymer | Poly | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
51 | Polymer Dose | PolyDose | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
61 | Ferric Chloride | FeCl3 | Day | Parameter | #/day | 1 | FALSE | [6 empty] | Avg
71 | Ferric Chloride | FeCl3 | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
81 | Ferric Chloride Dose | FeCl3Dose | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
91 | Potassium Permanganate | KmnO4 | Day | Parameter | #/day | 1 | FALSE | [6 empty] | Avg
101 | Potassium Permanganate | KmnO4 | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
111 | Potassium Permanganate Dose | KmnO4Dose | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
121 | Chlorine | Cl2 | Day | Parameter | #/day | 1 | FALSE | [6 empty] | Avg
131 | Chlorine Dose | Cl2Dose | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
141 | Sodium hypochlorite | NaOCl | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
151 | Sodium hypochlorite | NaOClDose | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
161 | Hydrofluoric acid | HF | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
171 | Hydrofluoric acid Dose | HF Dose | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
181 | Sodium hydroxide | NaOH | Day | Parameter | #/day | 1 | FALSE | [6 empty] | Avg
191 | Sodium hydroxide Dose | NaOH Dose | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
201 | Polyphosphates | PolyP | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
211 | Polyphosphates Dose | PolyPDose | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
221 | Fluorosilicic acid | H2SiF4 | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
231 | Fluorosilicic acid Dose | H2SiF4Ds | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
Avg
Avg
Avg
Avg
Avg
Avg
Note on E7: Select from: Day 4 Hours Hour 30 Minutes 15 Minutes 5 Minutes Minute
Note on F7: Select From: Parameter Text Parameter Calculated
Note on H7: 0 will be used if left blank
Note on P7: Select from: Min Max Total Avg First Last Start Value End Value
Note on Q7: Interface. Enter minimum value to use as filter. Ie if 0 is entered, values<0 will be ignored when importing data.
Note on R7: Ie if 9999 is entered, values>9999 will be ignored when importing data.
Note on S7: Enter a value by which the imported data will be multiplied to convert it to the proper units. Leave it blank if no change is necessary.
Note on I7: Set to 1, TRUE, or Y if the Parameter should allow data qualifiers (<,>, or ND)
Note on C7: Scott Dorner: Location and Parameter Name will create the variable name (up to 40 characters)
Note on G7: 10 Characters Max
Note on D7: 20 Characters Max, combined with Short (C2)
Note on B2: Combined with Parameter Name to make Variable Name
Note on B3: Combined with Short Name to make Heading

## Sed Basin,Floc
Location: | Sed Basin | Area Name:
Location Name | SB
Short Location Name | SB
Desc: | Sed Basin/ Flocculation
Base Var # | 4000
| Parameter | Short |  |  |  | Dec | Allow |  | Entry | Entry | Description | Storet |  |  | Low | High | Scale
Var # | Name | Name | Frequency | Type | Units | Plcs | Symbol | Equation | Min | max | (Notes) | Code | Scada Tag | Statistic | Range | Range | Factor
1 | Flow | Flow | Day | Parameter | MGD | 3 | FALSE |  |  |  |  | 50050 |  | Avg
2 | Flow | Flow | Day | Parameter | gpm | 1 | FALSE |  |  |  |  | 00058 |  | Avg
11 | Total Suspended Solids | TSS | Day | Parameter | mg/l | 0 | FALSE |  |  |  |  | 00530 |  | Avg
21 | Hardness (CaCO3) | Hard | Day | Parameter | mg/l | 0 | FALSE |  |  |  |  | 00900 |  | Avg
31 | Alkalinity (CaCO3) | Alkal | Day | Parameter | mg/l | 2 | FALSE |  |  |  |  | 00410 |  | Avg
41 | Turbidity 15 Min | Turb | 15 Minute | Parameter | NTU | 2 | FALSE |  |  |  |  | 82078 |  | Avg
42 | Turbidity | Turb | Day | Parameter | NTU | 2 | FALSE |  |  |  |  | 82078 |  | Avg
43 | Turbidity Hrly | Turb | Hour | Parameter | NTU | 2 | FALSE |  |  |  |  | 82078 |  | Avg
51 | Dissolved Oxygen | DO | Day | Parameter | mg/L | 2 | TRUE |  |  |  |  | 00300 |  | Avg
61 | Carbon Dioxide | CO2 | Day | Parameter | mg/L | 2 | TRUE |  |  |  |  | 00405 |  | Avg
71 | Arsenic | As | Day | Parameter | ug/l | 0 | TRUE |  |  |  |  | 01002 |  | Avg
81 | Chloride | Cl | Day | Parameter | mg/l | 2 | TRUE |  |  |  |  | 00940 |  | Avg
101 | Chlorine Residual Max | Cl2 Max | Day | Parameter | mg/L | 2 | FALSE |  |  |  |  | 50060 |  | Max
102 | Chlorine Residual Min | Cl2 Min | Day | Parameter | mg/L | 2 | FALSE |  |  |  |  | 50060 |  | Min
103 | Chlorine Residual Avg | Cl2 Avg | Day | Parameter | mg/L | 2 | FALSE |  |  |  |  | 50060 |  | Avg
111 | Color | Color | Day | Parameter | ColorUnits | 0 | FALSE |  |  |  |  | 00079 |  | Avg
121 | Corrosivity | Corros | Day | Parameter | WtrNum | 0 | FALSE |  |  |  |  | 71814 |  | Avg
131 | Fluoride | F- | Day | Parameter | mg/l | 3 | TRUE |  |  |  |  | 00951 |  | Avg
141 | Foaming Agents | Foam | Day | Parameter | mg/l | 2 | FALSE |  |  |  |  | 01288 |  | Avg
151 | Nitrate/Nitrite | NO 3/2 | Day | Parameter | mg/l | 2 | TRUE |  |  |  |  | 00630 |  | Avg
161 | Odor | Odor | Day | Parameter | Code | 0 | FALSE |  |  |  |  | 34773 |  | Avg
171 | Sulfate | SO4 | Day | Parameter | mg/l | 3 | TRUE |  |  |  |  | 00945 |  | Avg
181 | Total Dissolved Solids | TDS | Day | Parameter | mg/l | 2 | TRUE |  |  |  |  | 47004 |  | Avg
191 | pH | pH | Day | Parameter | SU | 1 | FALSE |  |  |  |  | 01092 |  | Avg
201 | Temperature | Temp | Day | Parameter | Deg F | 0 | FALSE |  |  |  |  | 00400 |  | Avg
211 | Temperature | Temp | Day | Parameter | Deg C | 0 | FALSE |  |  |  |  | 00011 |  | Avg
221 | Run Time | Run Time | Day | Parameter | hrs | 1 | FALSE |  |  |  |  | 00010 |  | Avg
231 | Zeta Potential | Zeta | Day | Parameter | mV | 0 | FALSE | [6 empty] | Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Avg
Note on E7: Select from: Day 4 Hours Hour 30 Minutes 15 Minutes 5 Minutes Minute
Note on F7: Select From: Parameter Text Parameter Calculated
Note on H7: 0 will be used if left blank
Note on P7: Select from: Min Max Total Avg First Last Start Value End Value
Note on Q7: Interface. Enter minimum value to use as filter. Ie if 0 is entered, values<0 will be ignored when importing data.
Note on R7: Ie if 9999 is entered, values>9999 will be ignored when importing data.
Note on S7: Enter a value by which the imported data will be multiplied to convert it to the proper units. Leave it blank if no change is necessary.
Note on I7: Set to 1, TRUE, or Y if the Parameter should allow data qualifiers (<,>, or ND)
Note on C7: Scott Dorner: Location and Parameter Name will create the variable name (up to 40 characters)
Note on G7: 10 Characters Max
Note on D7: 20 Characters Max, combined with Short (C2)
Note on B2: Combined with Parameter Name to make Variable Name
Note on B3: Combined with Short Name to make Heading

## Filter 1
Location: | Filter 1 | Area Name:
Location Name | F01
Short Location Name | F01
Desc: | Filter 1
Base Var # | 4100
| Parameter | Short |  |  |  | Dec | Allow |  | Entry | Entry | Description | Storet |  |  | Low | High | Scale
Var # | Name | Name | Frequency | Type | Units | Plcs | Symbol | Equation | Min | max | (Notes) | Code | Scada Tag | Statistic | Range | Range | Factor
1 | Flow Rate | Flow Rate | Day | Parameter | MGD | 1 | FALSE |  |  |  |  | 50050 |  | Avg
2 | Daily Total Flow | Daily Tot Flow | Day | Parameter | MGD | 1 | FALSE |  |  |  |  | 00058 |  | Avg
11 | Runtime | Run | Day | Parameter | Hours | 1 | FALSE |  |  |  |  | 00530 |  | Avg
21 | Backwash Time | Back Time | Day | Text Parameter | Time | 2 | FALSE |  |  |  |  | 00900 |  | Avg
25 | Runtime at Backwash | Back Run | Day | Parameter | Hours | 1 | FALSE |  |  |  |  | 00410 |  | Avg
41 | Filter to Waste Duration | Filt Wst Dur | Day | Parameter | Hours | 2 | FALSE |  |  |  |  | 82078 |  | Avg
42 | Filter to Waste Flow | Filt Wst Flw | Day | Parameter | Gals | 0 | FALSE |  |  |  |  | 82078 |  | Avg
51 | Turbidity | Turb | 15 Minute | Parameter | NTU | 3 | FALSE |  |  |  |  | 82078 |  | Avg
53 | Turbidity Lab | Turb Lab | Hourly | Parameter | NTU | 3 | FALSE |  |  |  |  | 00300 |  | Avg
61 | Wash Water Meter | Wsh Wat Met | Day | Parameter | MG | 3 | FALSE |  |  |  |  | 00405 |  | Avg
65 | Wash Water Used | Wsh Wat Met | Day | Parameter | MGD | 3 | FALSE |  |  |  |  | 01105 |  | Avg
71 | Surface Wash Water Meter | Surf Wat Used | Day | Parameter | MG | 3 | FALSE |  |  |  |  | 01002 |  | Avg
75 | Surface Wash Water Used | Surf Wat Used | Day | Parameter | MGD | 3 | FALSE |  |  |  |  | 00940 |  | Avg
81 | Headloss | Headloss | Day | Parameter | Ft | 2 | FALSE |  |  |  |  | 50060 |  | Max
Note on E7: Select from: Day 4 Hours Hour 30 Minutes 15 Minutes 5 Minutes Minute
Note on F7: Select From: Parameter Text Parameter Calculated
Note on H7: 0 will be used if left blank
Note on P7: Select from: Min Max Total Avg First Last Start Value End Value
Note on Q7: Interface. Enter minimum value to use as filter. Ie if 0 is entered, values<0 will be ignored when importing data.
Note on R7: Ie if 9999 is entered, values>9999 will be ignored when importing data.
Note on S7: Enter a value by which the imported data will be multiplied to convert it to the proper units. Leave it blank if no change is necessary.
Note on I7: Set to 1, TRUE, or Y if the Parameter should allow data qualifiers (<,>, or ND)
Note on C7: Scott Dorner: Location and Parameter Name will create the variable name (up to 40 characters)
Note on G7: 10 Characters Max
Note on D7: 20 Characters Max, combined with Short (C2)
Note on B2: Combined with Parameter Name to make Variable Name
Note on B3: Combined with Short Name to make Heading

## Filtered Water
Location: | Filtered Water | Area Name:
Location Name | Filt Wat
Short Location Name | FW
Desc: | Filtered Water
Base Var # | 6000
| Parameter | Short |  |  |  | Dec | Allow |  | Entry | Entry | Description | Storet |  |  | Low | High | Scale
Var # | Name | Name | Frequency | Type | Units | Plcs | Symbol | Equation | Min | max | (Notes) | Code | Scada Tag | Statistic | Range | Range | Factor
1 | Flow | Flow | Day | Parameter | MGD | 3 | FALSE |  |  |  |  | 50050 |  | Avg
11 | Flow | Flow | Day | Parameter | gpm | 1 | FALSE |  |  |  |  | 00058 |  | Avg
21 | Total Suspended Solids | TSS | Day | Parameter | mg/l | 0 | FALSE |  |  |  |  | 00530 |  | Avg
31 | Hardness (CaCO3) | Hard | Day | Parameter | mg/l | 2 | FALSE |  |  |  |  | 00900 |  | Avg
41 | Alkalinity (CaCO3) | Alkal | Day | Parameter | mg/l | 2 | FALSE |  |  |  |  | 00410 |  | Avg
51 | Turbidity 15 Min | Turb | Day | 15 Minute | NTU | 2 | FALSE |  |  |  |  | 82078 |  | Avg
61 | Turbidity | Turb | Day | Parameter | NTU | 2 | FALSE |  |  |  |  | 82078 |  | Avg
71 | Turbidity Hrly | Turb | Day | Hour | NTU | 2 | FALSE |  |  |  |  | 82078 |  | Avg
81 | Dissolved Oxygen | DO | Day | Parameter | mg/L | 2 | TRUE |  |  |  |  | 00300 |  | Avg
91 | Carbon Dioxide | CO2 | Day | Parameter | mg/L | 2 | TRUE |  |  |  |  | 00405 |  | Avg
101 | Aluminum | Al | Day | Parameter | ug/l | 2 | TRUE |  |  |  |  | 01105 |  | Avg
111 | Arsenic | As | Day | Parameter | ug/l | 0 | TRUE |  |  |  |  | 01002 |  | Avg
121 | Chloride | Cl | Day | Parameter | mg/l | 2 | TRUE |  |  |  |  | 00940 |  | Avg
131 | Chlorine Residual Max | Cl2 Max | Day | Parameter | mg/L | 2 | FALSE |  |  |  |  | 50060 |  | Max
141 | Chlorine Residual Min | Cl2 Min | Day | Parameter | mg/L | 2 | FALSE |  |  |  |  | 50060 |  | Min
151 | Chlorine Residual Avg | Cl2 Avg | Day | Parameter | mg/L | 2 | FALSE |  |  |  |  | 50060 |  | Avg
161 | Color | Color | Day | Parameter | ColorUnits | 0 | FALSE |  |  |  |  | 00079 |  | Avg
171 | Copper | Cu | Day | Parameter | ug/l | 0 | TRUE |  |  |  |  | 01042 |  | Avg
181 | Corrosivity | Corros | Day | Parameter | WtrNum | 0 | FALSE |  |  |  |  | 71814 |  | Avg
191 | Fluoride | F- | Day | Parameter | mg/l | 3 | TRUE |  |  |  |  | 00951 |  | Avg
201 | Foaming Agents | Foam | Day | Parameter | mg/l | 2 | FALSE |  |  |  |  | 01288 |  | Avg
211 | Iron | Fe | Day | Parameter | ug/l | 0 | TRUE |  |  |  |  | 01045 |  | Avg
221 | Lead | Pb | Day | Parameter | ug/l | 0 | TRUE |  |  |  |  | 01051 |  | Avg
231 | Manganese | Mn | Day | Parameter | ug/l | 0 | TRUE |  |  |  |  | 01055 |  | Avg
241 | Nitrate/Nitrite | NO 3/2 | Day | Parameter | mg/l | 2 | TRUE |  |  |  |  | 00630 |  | Avg
251 | Odor | Odor | Day | Parameter | Code | 0 | FALSE |  |  |  |  | 34773 |  | Avg
261 | Silver | Ag | Day | Parameter | ug/l | 0 | TRUE |  |  |  |  | 01077 |  | Avg
271 | Sulfate | SO4 | Day | Parameter | mg/l | 3 | TRUE |  |  |  |  | 00945 |  | Avg
281 | Total Dissolved Solids | TDS | Day | Parameter | mg/l | 2 | TRUE |  |  |  |  | 47004 |  | Avg
291 | Zinc | Zn | Day | Parameter | ug/l | 0 | TRUE |  |  |  |  | 01092 |  | Avg
301 | pH | pH | Day | Parameter | SU | 1 | FALSE |  |  |  |  | 00400 |  | Avg
311 | Temperature | Temp | Day | Parameter | Deg F | 0 | FALSE |  |  |  |  | 00011 |  | Avg
321 | Temperature | Temp | Day | Parameter | Deg C | 0 | FALSE |  |  |  |  | 00010 |  | Avg
331 | Run Time | Run Time | Day | Parameter | hrs | 1 | FALSE | [6 empty] | Avg
341 | Pumping Level | Pump Lvl | Day | Parameter | ft | 1 | FALSE | [6 empty] | Avg
351 | Static Level | Static Lvl | Day | Parameter | ft | 1 | FALSE | [6 empty] | Avg
361 | Hours at Rest | Hrs Rest | Day | Parameter | hrs | 2 | FALSE | [6 empty] | Avg
371 | Zeta Potential | Zeta | Day | Parameter | mV | 0 | FALSE | [6 empty] | Avg
381 | Power | Pwr | Day | Parameter | kwH | 2 | FALSE | [6 empty] | Avg
391 | Average Level | AvgLvl | Day | Parameter | ft | 1 | FALSE | [6 empty] | Avg
401 | Minimum Level | MinLvl | Day | Parameter | ft | 1 | FALSE | [6 empty] | Avg
411 | Maximum Level | MaxLvl | Day | Parameter | ft | 1 | FALSE | [6 empty] | Avg
421 | Average Pressure | AvgPress | Day | Parameter | psi | 0 | FALSE | [6 empty] | Avg
431 | Minimum Pressure | MinPress | Day | Parameter | psi | 0 | FALSE | [6 empty] | Avg
441 | Maximum Pressure | MaxPress | Day | Parameter | psi | 0 | FALSE | [6 empty] | Avg
451 | Alum | Alum | Day | Parameter | #/day | 1 | FALSE | [6 empty] | Avg
461 | Alum | Alum | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
471 | Alum Dose | AlumDose | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
481 | Polymer | Poly | Day | Parameter | #/day | 1 | FALSE | [6 empty] | Avg
491 | Polymer | Poly | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
501 | Polymer Dose | PolyDose | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
511 | Ferric Chloride | FeCl3 | Day | Parameter | #/day | 1 | FALSE | [6 empty] | Avg
521 | Ferric Chloride | FeCl3 | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
531 | Ferric Chloride Dose | FeCl3Dose | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
541 | Potassium Permanganate | KmnO4 | Day | Parameter | #/day | 1 | FALSE | [6 empty] | Avg
551 | Potassium Permanganate | KmnO4 | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
561 | Potassium Permanganate Dose | KmnO4Dose | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
571 | Chlorine | Cl2 | Day | Parameter | #/day | 1 | FALSE | [6 empty] | Avg
581 | Chlorine Dose | Cl2Dose | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
591 | Sodium hypochlorite | NaOCl | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
601 | Sodium hypochlorite | NaOClDose | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
611 | Hydrofluoric acid | HF | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
621 | Hydrofluoric acid Dose | HF Dose | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
631 | Sodium hydroxide | NaOH | Day | Parameter | #/day | 1 | FALSE | [6 empty] | Avg
641 | Sodium hydroxide Dose | NaOH Dose | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
651 | Polyphosphates | PolyP | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
661 | Polyphosphates Dose | PolyPDose | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
671 | Fluorosilicic acid | H2SiF4 | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
681 | Fluorosilicic acid Dose | H2SiF4Ds | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
691 | Surface Loading Rate | SurfLdg | Day | Parameter | gpd/ft2 | 2 | FALSE | [6 empty] | Avg
701 | Operator on Duty | Operator | Day | Parameter | Initials | 0 | FALSE | [6 empty] | Avg
711 | # of Backwashes | # BW | Day | Parameter | Count | 0 | FALSE | [6 empty] | Avg
721 | Status | Status | Hour | Parameter | Status | 0 | FALSE | [6 empty] | Avg
731 | RunTime at Backwash | RT @ BW | Day | Parameter | Hours | 1 | FALSE | [6 empty] | Avg
741 | RunTime Since Backwash | RT Since BW | Day | Parameter | Hours | 1 | FALSE | [6 empty] | Avg
751 | Segment Volume | Vol | Day | Calculated | MG | 1 | FALSE
761 | T10 | T10 | Day | Calculated | Mins | 1 | FALSE | ((Segment Vol (MG) / Flow (MGD) ) *24 * 60) * Baffling Factor
771 | CT Achieved | CT Achvd | Day | Calculated | mg/L - mins | 1 | FALSE | CL2 Residual (mg/L) * T10 (mins)
781 | 3 Log Giardia CT Required | 3L CT Req | Day | Calculated | mg/L - mins | 1 | FALSE | Final Temperature, pH, CL2
791 | 4 Log Viruses CT Required | 4 Log CT Req | Day | Calculated | mg/L - mins | 1 | FALSE | Table for Inactivation of viruses
801 | 3 Log Giardia CT Ratio | 3 Log CT Ratio | Day | Calculated | Ratio | 1 | FALSE | CT Achieved / 3 Log Giardia CT Required
811 | 4 Log Viruses CT Ratio | 4 Log CT Ratio | Day | Calculated | Ratio | 1 | FALSE | CT Achieved / 4 Log CT Required
821 | Giardia Log Inactivation | Gia Inact | Day | Calculated | Units | 1 | FALSE | 3 * 3 Log Giardia CT Ratio
831 | Viruses Log Inactivation |  | Day | Calculated | Units | 1 | FALSE | 3 * 4 Log Viruses Ratio
841 | Filtered Water Tutbidity | Filt H20 Turbid | Hour | Parameter | NTU | 2 | FALSE
851 | Filtered Wtr Turbidity Count <95% Limit | Filt Turb | Day | Calculated | Count | 0 | FALSE
861 | Filtered Water pH Maximum | pH Filt max | Day | Parameter | SU | 2 | FALSE
871 | Filtered Water pH Minimum | pH Filt min | Day | Parameter | SU | 2 | FALSE
881 | Filtered Water pH Average | pH Filt avg | Day | Parameter | SU | 2 | FALSE
Note on E7: Select from: Day 4 Hours Hour 30 Minutes 15 Minutes 5 Minutes Minute
Note on F7: Select From: Parameter Text Parameter Calculated
Note on H7: 0 will be used if left blank
Note on P7: Select from: Min Max Total Avg First Last Start Value End Value
Note on Q7: Interface. Enter minimum value to use as filter. Ie if 0 is entered, values<0 will be ignored when importing data.
Note on R7: Ie if 9999 is entered, values>9999 will be ignored when importing data.
Note on S7: Enter a value by which the imported data will be multiplied to convert it to the proper units. Leave it blank if no change is necessary.
Note on I7: Set to 1, TRUE, or Y if the Parameter should allow data qualifiers (<,>, or ND)
Note on C7: Scott Dorner: Location and Parameter Name will create the variable name (up to 40 characters)
Note on G7: 10 Characters Max
Note on D7: 20 Characters Max, combined with Short (C2)
Note on B2: Combined with Parameter Name to make Variable Name
Note on B3: Combined with Short Name to make Heading

## CCB
Location: | CCB | Area Name:
Location Name | CCB
Short Location Name | CCB
Desc: | Chlorine Contact Basin
Base Var # | 7000
| Parameter | Short |  |  |  | Dec | Allow |  | Entry | Entry | Description | Storet |  |  | Low | High | Scale
Var # | Name | Name | Frequency | Type | Units | Plcs | Symbol | Equation | Min | max | (Notes) | Code | Scada Tag | Statistic | Range | Range | Factor
1 | Flow | Flow | Day | Parameter | MGD | 3 | FALSE |  |  |  |  | 50050 |  | Avg
11 | Flow | Flow | Day | Parameter | gpm | 1 | FALSE |  |  |  |  | 00058 |  | Avg
21 | Hardness (CaCO3) | Hard | Day | Parameter | mg/l | 0 | FALSE |  |  |  |  | 00900 |  | Avg
31 | Alkalinity (CaCO3) | Alkal | Day | Parameter | mg/l | 2 | FALSE |  |  |  |  | 00410 |  | Avg
41 | Turbidity 15 Min | Turb | 15 Minute | Parameter | NTU | 2 | FALSE |  |  |  |  | 82078 |  | Avg
51 | Turbidity | Turb | Day | Parameter | NTU | 2 | FALSE |  |  |  |  | 82078 |  | Avg
61 | Turbidity Hrly | Turb | Day | Parameter | NTU | 2 | FALSE |  |  |  |  | 82078 |  | Avg
71 | Dissolved Oxygen | DO | Day | Parameter | mg/L | 2 | TRUE |  |  |  |  | 00300 |  | Avg
81 | Carbon Dioxide | CO2 | Day | Parameter | mg/L | 2 | TRUE |  |  |  |  | 00405 |  | Avg
91 | Aluminum | Al | Day | Parameter | ug/l | 2 | TRUE |  |  |  |  | 01105 |  | Avg
101 | Arsenic | As | Day | Parameter | ug/l | 0 | TRUE |  |  |  |  | 01002 |  | Avg
111 | Chloride | Cl | Day | Parameter | mg/l | 2 | TRUE |  |  |  |  | 00940 |  | Avg
121 | Chlorine Residual Max | Cl2 Max | Day | Parameter | mg/L | 2 | FALSE |  |  |  |  | 50060 |  | Max
131 | Chlorine Residual Min | Cl2 Min | Day | Parameter | mg/L | 2 | FALSE |  |  |  |  | 50060 |  | Min
141 | Chlorine Residual Avg | Cl2 Avg | Day | Parameter | mg/L | 2 | FALSE |  |  |  |  | 50060 |  | Avg
151 | Color | Color | Day | Parameter | ColorUnits | 0 | FALSE |  |  |  |  | 00079 |  | Avg
161 | Copper | Cu | Day | Parameter | ug/l | 0 | TRUE |  |  |  |  | 01042 |  | Avg
171 | Corrosivity | Corros | Day | Parameter | WtrNum | 0 | FALSE |  |  |  |  | 71814 |  | Avg
181 | Fluoride | F- | Day | Parameter | mg/l | 3 | TRUE |  |  |  |  | 00951 |  | Avg
191 | Foaming Agents | Foam | Day | Parameter | mg/l | 2 | FALSE |  |  |  |  | 01288 |  | Avg
201 | Iron | Fe | Day | Parameter | ug/l | 0 | TRUE |  |  |  |  | 01045 |  | Avg
211 | Lead | Pb | Day | Parameter | ug/l | 0 | TRUE |  |  |  |  | 01051 |  | Avg
221 | Manganese | Mn | Day | Parameter | ug/l | 0 | TRUE |  |  |  |  | 01055 |  | Avg
231 | Nitrate/Nitrite | NO 3/2 | Day | Parameter | mg/l | 2 | TRUE |  |  |  |  | 00630 |  | Avg
241 | Odor | Odor | Day | Parameter | Code | 0 | FALSE |  |  |  |  | 34773 |  | Avg
251 | Silver | Ag | Day | Parameter | ug/l | 0 | TRUE |  |  |  |  | 01077 |  | Avg
261 | Sulfate | SO4 | Day | Parameter | mg/l | 3 | TRUE |  |  |  |  | 00945 |  | Avg
271 | Total Dissolved Solids | TDS | Day | Parameter | mg/l | 2 | TRUE |  |  |  |  | 47004 |  | Avg
281 | Zinc | Zn | Day | Parameter | ug/l | 0 | TRUE |  |  |  |  | 01092 |  | Avg
291 | pH | pH | Day | Parameter | SU | 1 | FALSE |  |  |  |  | 00400 |  | Avg
301 | Temperature | Temp | Day | Parameter | Deg F | 0 | FALSE |  |  |  |  | 00011 |  | Avg
311 | Temperature | Temp | Day | Parameter | Deg C | 0 | FALSE |  |  |  |  | 00010 |  | Avg
321 | Chlorine | Cl2 | Day | Parameter | #/day | 1 | FALSE | [6 empty] | Avg
331 | Chlorine Dose | Cl2Dose | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
341 | Segment Volume | Vol | Day | Calculated | MG | 1 | FALSE
351 | T10 | T10 | Day | Calculated | Mins | 1 | FALSE | ((Segment Vol (MG) / Flow (MGD) ) *24 * 60) * Baffling Factor
361 | CT Achieved | CT Achvd | Day | Calculated | mg/L - mins | 1 | FALSE | CL2 Residual (mg/L) * T10 (mins)
371 | 3 Log Giardia CT Required | 3L CT Req | Day | Calculated | mg/L - mins | 1 | FALSE | Final Temperature, pH, CL2
381 | 4 Log Viruses CT Required | 4 Log CT Req | Day | Calculated | mg/L - mins | 1 | FALSE | Table for Inactivation of viruses
391 | 3 Log Giardia CT Ratio | 3 Log CT Ratio | Day | Calculated | Ratio | 1 | FALSE | CT Achieved / 3 Log Giardia CT Required
401 | 4 Log Viruses CT Ratio | 4 Log CT Ratio | Day | Calculated | Ratio | 1 | FALSE | CT Achieved / 4 Log CT Required
411 | Giardia Log Inactivation | Gia Inact | Day | Calculated | Units | 1 | FALSE | 3 * 3 Log Giardia CT Ratio
421 | Viruses Log Inactivation |  | Day | Calculated | Units | 1 | FALSE | 3 * 4 Log Viruses Ratio
Note on E7: Select from: Day 4 Hours Hour 30 Minutes 15 Minutes 5 Minutes Minute
Note on F7: Select From: Parameter Text Parameter Calculated
Note on H7: 0 will be used if left blank
Note on P7: Select from: Min Max Total Avg First Last Start Value End Value
Note on Q7: Interface. Enter minimum value to use as filter. Ie if 0 is entered, values<0 will be ignored when importing data.
Note on R7: Ie if 9999 is entered, values>9999 will be ignored when importing data.
Note on S7: Enter a value by which the imported data will be multiplied to convert it to the proper units. Leave it blank if no change is necessary.
Note on I7: Set to 1, TRUE, or Y if the Parameter should allow data qualifiers (<,>, or ND)
Note on C7: Scott Dorner: Location and Parameter Name will create the variable name (up to 40 characters)
Note on G7: 10 Characters Max
Note on D7: 20 Characters Max, combined with Short (C2)
Note on B2: Combined with Parameter Name to make Variable Name
Note on B3: Combined with Short Name to make Heading

## Final
Location: | Final | Area Name:
Location Name | Final
Short Location Name | Final
Desc: | Effluent
Base Var # | 8000
| Parameter | Short |  |  |  | Dec | Allow |  | Entry | Entry | Description | Storet |  |  | Low | High | Scale
Var # | Name | Name | Frequency | Type | Units | Plcs | Symbol | Equation | Min | max | (Notes) | Code | Scada Tag | Statistic | Range | Range | Factor
1 | Flow | Flow | Day | Parameter | MGD | 3 | FALSE |  |  |  |  | 50050 |  | Avg
11 | Flow | Flow | Day | Parameter | gpm | 1 | FALSE |  |  |  |  | 00058 |  | Avg
21 | Total Suspended Solids | TSS | Day | Parameter | mg/l | 0 | FALSE |  |  |  |  | 00530 |  | Avg
31 | Hardness (CaCO3) | Hard | Day | Parameter | mg/l | 0 | FALSE |  |  |  |  | 00900 |  | Avg
41 | Alkalinity (CaCO3) | Alkal | Day | Parameter | mg/l | 2 | FALSE |  |  |  |  | 00410 |  | Avg
51 | Turbidity 15 Min | Turb | 15 Minute | Parameter | NTU | 2 | FALSE |  |  |  |  | 82078 |  | Avg
61 | Turbidity | Turb | Day | Parameter | NTU | 2 | FALSE |  |  |  |  | 82078 |  | Avg
71 | Turbidity Hrly | Turb | Hour | Parameter | NTU | 2 | FALSE |  |  |  |  | 82078 |  | Avg
81 | Dissolved Oxygen | DO | Day | Parameter | mg/L | 2 | FALSE |  |  |  |  | 00300 |  | Avg
91 | Carbon Dioxide | CO2 | Day | Parameter | mg/L | 2 | TRUE |  |  |  |  | 00405 |  | Avg
101 | Aluminum | Al | Day | Parameter | ug/l | 2 | TRUE |  |  |  |  | 01105 |  | Avg
111 | Arsenic | As | Day | Parameter | ug/l | 0 | TRUE |  |  |  |  | 01002 |  | Avg
121 | Chloride | Cl | Day | Parameter | mg/l | 2 | TRUE |  |  |  |  | 00940 |  | Avg
131 | Chlorine Residual Max | Cl2 Max | Day | Parameter | mg/L | 2 | FALSE |  |  |  |  | 50060 |  | Max
141 | Chlorine Residual Min | Cl2 Min | Day | Parameter | mg/L | 2 | FALSE |  |  |  |  | 50060 |  | Min
151 | Chlorine Residual Avg | Cl2 Avg | Day | Parameter | mg/L | 2 | FALSE |  |  |  |  | 50060 |  | Avg
161 | Color | Color | Day | Parameter | ColorUnits | 0 | FALSE |  |  |  |  | 00079 |  | Avg
171 | Copper | Cu | Day | Parameter | ug/l | 0 | TRUE |  |  |  |  | 01042 |  | Avg
181 | Corrosivity | Corros | Day | Parameter | WtrNum | 0 | FALSE |  |  |  |  | 71814 |  | Avg
191 | Fluoride | F- | Day | Parameter | mg/l | 3 | TRUE |  |  |  |  | 00951 |  | Avg
201 | Foaming Agents | Foam | Day | Parameter | mg/l | 2 | FALSE |  |  |  |  | 01288 |  | Avg
211 | Iron | Fe | Day | Parameter | ug/l | 0 | TRUE |  |  |  |  | 01045 |  | Avg
221 | Lead | Pb | Day | Parameter | ug/l | 0 | TRUE |  |  |  |  | 01051 |  | Avg
231 | Manganese | Mn | Day | Parameter | ug/l | 0 | TRUE |  |  |  |  | 01055 |  | Avg
241 | Nitrate/Nitrite | NO 3/2 | Day | Parameter | mg/l | 2 | TRUE |  |  |  |  | 00630 |  | Avg
251 | Odor | Odor | Day | Parameter | Code | 0 | FALSE |  |  |  |  | 34773 |  | Avg
261 | Silver | Ag | Day | Parameter | ug/l | 0 | TRUE |  |  |  |  | 01077 |  | Avg
271 | Sulfate | SO4 | Day | Parameter | mg/l | 3 | TRUE |  |  |  |  | 00945 |  | Avg
281 | Total Dissolved Solids | TDS | Day | Parameter | mg/l | 2 | TRUE |  |  |  |  | 47004 |  | Avg
291 | Zinc | Zn | Day | Parameter | ug/l | 0 | TRUE |  |  |  |  | 01092 |  | Avg
301 | pH | pH | Day | Parameter | SU | 1 | FALSE |  |  |  |  | 00400 |  | Avg
311 | Temperature | Temp | Day | Parameter | Deg F | 0 | FALSE |  |  |  |  | 00011 |  | Avg
321 | Temperature | Temp | Day | Parameter | Deg C | 0 | FALSE |  |  |  |  | 00010 |  | Avg
331 | Run Time | Run Time | Day | Parameter | hrs | 1 | FALSE | [6 empty] | Avg
341 | Pumping Level | Pump Lvl | Day | Parameter | ft | 1 | FALSE | [6 empty] | Avg
351 | Static Level | Static Lvl | Day | Parameter | ft | 1 | FALSE | [6 empty] | Avg
361 | Hours at Rest | Hrs Rest | Day | Parameter | hrs | 2 | FALSE | [6 empty] | Avg
371 | Zeta Potential | Zeta | Day | Parameter | mV | 0 | FALSE | [6 empty] | Avg
381 | Power | Pwr | Day | Parameter | kwH | 2 | FALSE | [6 empty] | Avg
391 | Average Level | AvgLvl | Day | Parameter | ft | 1 | FALSE | [6 empty] | Avg
401 | Minimum Level | MinLvl | Day | Parameter | ft | 1 | FALSE | [6 empty] | Avg
411 | Maximum Level | MaxLvl | Day | Parameter | ft | 1 | FALSE | [6 empty] | Avg
421 | Average Pressure | AvgPress | Day | Parameter | psi | 0 | FALSE | [6 empty] | Avg
431 | Minimum Pressure | MinPress | Day | Parameter | psi | 0 | FALSE | [6 empty] | Avg
441 | Maximum Pressure | MaxPress | Day | Parameter | psi | 0 | FALSE | [6 empty] | Avg
451 | Alum | Alum | Day | Parameter | #/day | 1 | FALSE | [6 empty] | Avg
461 | Alum | Alum | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
471 | Alum Dose | AlumDose | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
481 | Polymer | Poly | Day | Parameter | #/day | 1 | FALSE | [6 empty] | Avg
491 | Polymer | Poly | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
501 | Polymer Dose | PolyDose | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
511 | Ferric Chloride | FeCl3 | Day | Parameter | #/day | 1 | FALSE | [6 empty] | Avg
521 | Ferric Chloride | FeCl3 | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
531 | Ferric Chloride Dose | FeCl3Dose | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
541 | Potassium Permanganate | KmnO4 | Day | Parameter | #/day | 1 | FALSE | [6 empty] | Avg
551 | Potassium Permanganate | KmnO4 | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
561 | Potassium Permanganate Dose | KmnO4Dose | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
571 | Chlorine | Cl2 | Day | Parameter | #/day | 1 | FALSE | [6 empty] | Avg
581 | Chlorine Dose | Cl2Dose | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
591 | Sodium hypochlorite | NaOCl | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
601 | Sodium hypochlorite | NaOClDose | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
611 | Hydrofluoric acid | HF | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
621 | Hydrofluoric acid Dose | HF Dose | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
631 | Sodium hydroxide | NaOH | Day | Parameter | #/day | 1 | FALSE | [6 empty] | Avg
641 | Sodium hydroxide Dose | NaOH Dose | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
651 | Polyphosphates | PolyP | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
661 | Polyphosphates Dose | PolyPDose | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
671 | Fluorosilicic acid | H2SiF4 | Day | Parameter | gal/day | 1 | FALSE | [6 empty] | Avg
681 | Fluorosilicic acid Dose | H2SiF4Ds | Day | Parameter | mg/l | 0 | FALSE | [6 empty] | Avg
691 | Surface Loading Rate | SurfLdg | Day | Parameter | gpd/ft2 | 2 | FALSE | [6 empty] | Avg
701 | Operator on Duty | Operator | Day | Parameter | Initials | 0 | FALSE | [6 empty] | Avg
711 | # of Backwashes | # BW | Day | Parameter | Count | 0 | FALSE | [6 empty] | Avg
721 | Status | Status | Hour | Parameter | Status | 0 | FALSE | [6 empty] | Avg
731 | RunTime at Backwash | RT @ BW | Day | Parameter | Hours | 1 | FALSE | [6 empty] | Avg
741 | RunTime Since Backwash | RT Since BW | Day | Parameter | Hours | 1 | FALSE | [6 empty] | Avg
751 | Segment Volume | Vol | Day | Calculated | MG | 1 | FALSE
761 | T10 | T10 | Day | Calculated | Mins | 1 | FALSE | ((Segment Vol (MG) / Flow (MGD) ) *24 * 60) * Baffling Factor
771 | CT Achieved | CT Achvd | Day | Calculated | mg/L - mins | 1 | FALSE | CL2 Residual (mg/L) * T10 (mins)
781 | 3 Log Giardia CT Required | 3L CT Req | Day | Calculated | mg/L - mins | 1 | FALSE | Final Temperature, pH, CL2
791 | 4 Log Viruses CT Required | 4 Log CT Req | Day | Calculated | mg/L - mins | 1 | FALSE | Table for Inactivation of viruses
801 | 3 Log Giardia CT Ratio | 3 Log CT Ratio | Day | Calculated | Ratio | 1 | FALSE | CT Achieved / 3 Log Giardia CT Required
811 | 4 Log Viruses CT Ratio | 4 Log CT Ratio | Day | Calculated | Ratio | 1 | FALSE | CT Achieved / 4 Log CT Required
821 | Giardia Log Inactivation | Gia Inact | Day | Calculated | Units | 1 | FALSE | 3 * 3 Log Giardia CT Ratio
831 | Viruses Log Inactivation |  | Day | Calculated | Units | 1 | FALSE | 3 * 4 Log Viruses Ratio
900 | 2,4-D |  | Quarterly | Parameter | mg/L | 3 | TRUE
901 | 2,4,5-TP (Silvex) | Silvex | Quarterly | Parameter | mg/L | 3 | TRUE
902 | Acrylamide |  | Quarterly | Parameter | mg/L | 3 | TRUE
903 | Alachlor |  | Quarterly | Parameter | mg/L | 3 | TRUE
904 | Atrazine |  | Quarterly | Parameter | mg/L | 3 | TRUE
905 | Bentazon |  | Quarterly | Parameter | mg/L | 3 | TRUE
906 | Carbofuran |  | Quarterly | Parameter | mg/L | 3 | TRUE
907 | Chlordane |  | Quarterly | Parameter | mg/L | 3 | TRUE
908 | Dalapon |  | Quarterly | Parameter | mg/L | 3 | TRUE
909 | Dibromochloro-propane (DBCP) | DBCP | Quarterly | Parameter | mg/L | 3 | TRUE
910 | Dinoseb |  | Quarterly | Parameter | mg/L | 3 | TRUE
911 | Diquat |  | Quarterly | Parameter | mg/L | 3 | TRUE
912 | Endothall |  | Quarterly | Parameter | mg/L | 3 | TRUE
913 | Endrin |  | Quarterly | Parameter | mg/L | 3 | TRUE
914 | Epichlorohydrin |  | Quarterly | Parameter | mg/L | 3 | TRUE
915 | Ethylene dibromide (EDB) | EDB | Quarterly | Parameter | mg/L | 3 | TRUE
916 | Glyphosate |  | Quarterly | Parameter | mg/L | 3 | TRUE
917 | Heptachlor |  | Quarterly | Parameter | mg/L | 3 | TRUE
918 | Heptachlor epoxide |  | Quarterly | Parameter | mg/L | 3 | TRUE
919 | Lindane |  | Quarterly | Parameter | mg/L | 3 | TRUE
920 | Methoxychlor |  | Quarterly | Parameter | mg/L | 3 | TRUE
921 | Molinate (Ordram) | Ordram | Quarterly | Parameter | mg/L | 3 | TRUE
922 | Oxamyl (Vydate) | Vydate | Quarterly | Parameter | mg/L | 3 | TRUE
923 | Pentachlorophenol |  | Quarterly | Parameter | mg/L | 3 | TRUE
924 | Picloram |  | Quarterly | Parameter | mg/L | 3 | TRUE
925 | Polychlorinated Biphenyls (PCBs) | PCBs | Quarterly | Parameter | mg/L | 3 | TRUE |  |  |  |  | 39516
926 | Simazine |  | Quarterly | Parameter | mg/L | 3 | TRUE
927 | Thiobencarb |  | Quarterly | Parameter | mg/L | 3 | TRUE
928 | Toxaphene |  | Quarterly | Parameter | mg/L | 3 | TRUE
929 | Benzo(a)pyrene (PAH) | PAH | Quarterly | Parameter | mg/L | 3 | TRUE
930 | Di(2-ethylhexyl)adipate |  | Quarterly | Parameter | mg/L | 3 | TRUE
931 | Di(2-ethylhexyl)phthalate |  | Quarterly | Parameter | mg/L | 3 | TRUE
932 | Hexachlorobenzene |  | Quarterly | Parameter | mg/L | 3 | TRUE
933 | Hexachloro-cyclopentadiene |  | Quarterly | Parameter | mg/L | 3 | TRUE
934 | 2,3,7,8-TCDD(Dioxin) | Dioxin | Quarterly | Parameter | mg/L | 3 | TRUE
935 | Benzene |  | Quarterly | Parameter | mg/L | 3 | TRUE
936 | Carbon Tetrachloride |  | Quarterly | Parameter | mg/L | 3 | TRUE
937 | o-Dichlorobenzene |  | Quarterly | Parameter | mg/L | 3 | TRUE
938 | p-Dichlorobenzene |  | Quarterly | Parameter | mg/L | 3 | TRUE
939 | 1,1-Dichloroethane |  | Quarterly | Parameter | mg/L | 3 | TRUE
940 | 1,2-Dichloroethane |  | Quarterly | Parameter | mg/L | 3 | TRUE
941 | 1,1-Dichloroethylene |  | Quarterly | Parameter | mg/L | 3 | TRUE
942 | cis-1,2-Di-chloroethylene |  | Quarterly | Parameter | mg/L | 3 | TRUE
943 | trans-1,2-Di-chloroethylene |  | Quarterly | Parameter | mg/L | 3 | TRUE
944 | Dichloromethane (methylene chloride) |  | Quarterly | Parameter | mg/L | 3 | TRUE
945 | 1,2-Dichloropropane |  | Quarterly | Parameter | mg/L | 3 | TRUE
946 | 1,3-Dichloropropene |  | Quarterly | Parameter | mg/L | 3 | TRUE
947 | Ethylbenzene |  | Quarterly | Parameter | mg/L | 3 | TRUE
948 | Methyl-tert-butyl-ether (MTBE) (d) | MTBE | Quarterly | Parameter | mg/L | 3 | TRUE
949 | Monochloro-benzene |  | Quarterly | Parameter | mg/L | 3 | TRUE
950 | Styrene |  | Quarterly | Parameter | mg/L | 3 | TRUE
951 | 1,1,2,2-Tetra-chloroethane |  | Quarterly | Parameter | mg/L | 3 | TRUE
952 | Tetrachloroethylene (PCE) | PCE | Quarterly | Parameter | mg/L | 3 | TRUE
953 | Toluene (e) |  | Quarterly | Parameter | mg/L | 3 | TRUE
954 | 1,2,4-Trichloro-benzene |  | Quarterly | Parameter | mg/L | 3 | TRUE
955 | 1,1,1-Trichloro-ethane |  | Quarterly | Parameter | mg/L | 3 | TRUE
956 | 1,1,2-Trichloro-ethane |  | Quarterly | Parameter | mg/L | 3 | TRUE
957 | Trichloroethylene (TCE) | TCE | Quarterly | Parameter | mg/L | 3 | TRUE
958 | Trichlorofluoro-methane |  | Quarterly | Parameter | mg/L | 3 | TRUE
959 | 1,1,2-Trichloro-1,2,2-trifluoroethane |  | Quarterly | Parameter | mg/L | 3 | TRUE
960 | Vinyl chloride |  | Quarterly | Parameter | mg/L | 3 | TRUE
961 | Xylenes |  | Quarterly | Parameter | mg/L | 3 | TRUE
962 | Aluminum |  | Quarterly | Parameter | mg/L | 3 | TRUE
963 | Antimony |  | Quarterly | Parameter | mg/L | 3 | TRUE
964 | Arsenic |  | Quarterly | Parameter | mg/L | 3 | TRUE
965 | Asbestos |  | Quarterly | Parameter | mg/L | 3 | TRUE
966 | Barium |  | Quarterly | Parameter | mg/L | 3 | TRUE
967 | Beryllium |  | Quarterly | Parameter | mg/L | 3 | TRUE
968 | Cadmium |  | Quarterly | Parameter | mg/L | 3 | TRUE
969 | Chromium |  | Quarterly | Parameter | mg/L | 3 | TRUE
970 | Cyanide |  | Quarterly | Parameter | mg/L | 3 | TRUE
971 | Fluoride |  | Quarterly | Parameter | mg/L | 3 | TRUE
972 | Mercury |  | Quarterly | Parameter | mg/L | 3 | TRUE
973 | Nickel |  | Quarterly | Parameter | mg/L | 3 | TRUE
974 | Nitrate (as Nitrate) |  | Quarterly | Parameter | mg/L | 3 | TRUE
975 | Selenium |  | Quarterly | Parameter | mg/L | 3 | TRUE
976 | Thallium |  | Quarterly | Parameter | mg/L | 3 | TRUE
977 | Gross Alpha Particle Activity |  | Quarterly | Parameter | mg/L | 3 | TRUE
978 | Gross Beta Particle Activity |  | Quarterly | Parameter | mg/L | 3 | TRUE
979 | Combined Radium |  | Quarterly | Parameter | mg/L | 3 | TRUE
980 | Strontium-90 |  | Quarterly | Parameter | mg/L | 3 | TRUE
981 | Tritium |  | Quarterly | Parameter | mg/L | 3 | TRUE
982 | Uranium |  | Quarterly | Parameter | mg/L | 3 | TRUE
983 | Total Trihalomethanes (TTHM) |  | Quarterly | Parameter | mg/L | 3 | TRUE
984 | Bromodichloromethane |  | Quarterly | Parameter | mg/L | 3 | TRUE
985 | Bromoform |  | Quarterly | Parameter | mg/L | 3 | TRUE
986 | Chloroform |  | Quarterly | Parameter | mg/L | 3 | TRUE
987 | Dibromochloromethane |  | Quarterly | Parameter | mg/L | 3 | TRUE
988 | Halloacetic Acids (5) (HAA5) |  | Quarterly | Parameter | mg/L | 3 | TRUE
989 | Monochloroacetic Acid |  | Quarterly | Parameter | mg/L | 3 | TRUE
990 | Dichloroacetic Acid |  | Quarterly | Parameter | mg/L | 3 | TRUE
991 | Trichloroacetic Acid |  | Quarterly | Parameter | mg/L | 3 | TRUE
992 | Monobromoacetic Acid |  | Quarterly | Parameter | mg/L | 3 | TRUE
993 | Dibromoacetic Acid |  | Quarterly | Parameter | mg/L | 3 | TRUE
994 | Bromate |  | Quarterly | Parameter | mg/L | 3 | TRUE
995 | Chlorite |  | Quarterly | Parameter | mg/L | 3 | TRUE
996 | Control of DBP Precursors (TOC) |  | Quarterly | Parameter | mg/L | 3 | TRUE
997 | Chloride |  | Quarterly | Parameter | mg/L | 3 | TRUE
998 | Corrosivity |  | Quarterly | Parameter | mg/L | 3 | TRUE
999 | Foaming Agents (MBAS) |  | Quarterly | Parameter | mg/L | 3 | TRUE
1000 | Manganese |  | Quarterly | Parameter | mg/L | 3 | TRUE
1001 | Methyl-tert-butyl-ether (MTBE) | MTBE | Quarterly | Parameter | mg/L | 3 | TRUE
1002 | Specific Conductance |  | Quarterly | Parameter | mg/L | 3 | TRUE
1003 | Thiobencarb |  | Quarterly | Parameter | mg/L | 3 | TRUE
1004 | Odor Threshold |  | Quarterly | Parameter | mg/L | 3 | TRUE
1005 | Boron |  | Quarterly | Parameter | mg/L | 3 | TRUE
1006 | Chromium VI | Cr6 | Quarterly | Parameter | mg/L | 3 | TRUE
1007 | Dichlorodifluoro-methane (Freon 12) |  | Quarterly | Parameter | mg/L | 3 | TRUE
1008 | Ethyl-tert-butyl-ether (ETBE) |  | Quarterly | Parameter | mg/L | 3 | TRUE
1009 | Perchlorate |  | Quarterly | Parameter | mg/L | 3 | TRUE
1010 | tert-Amyl-methyl-ether (TAME) |  | Quarterly | Parameter | mg/L | 3 | TRUE
1011 | tert-Butyl alcohol (TBA) |  | Quarterly | Parameter | mg/L | 3 | TRUE
1012 | Trichloropropane (1,2,3-TCP) |  | Quarterly | Parameter | mg/L | 3 | TRUE
1013 | Vanadium |  | Quarterly | Parameter | mg/L | 3 | TRUE
1014 | Giardia | Giardia | Quarterly | Parameter | mg/L | 3 | TRUE
1015 | Cryptosporidium | Crypto | Quarterly | Parameter | mg/L | 3 | TRUE
1016 | Bicarbonate |  | Quarterly | Parameter | mg/L | 3 | TRUE
1017 | Carbonate |  | Quarterly | Parameter | mg/L | 3 | TRUE
1018 | Hydroxide |  | Quarterly | Parameter | mg/L | 3 | TRUE
1019 | Potassium |  | Quarterly | Parameter | mg/L | 3 | TRUE
1020 | Radon (h) |  | Quarterly | Parameter | mg/L | 3 | TRUE
45 | Total Organic Carbon | TOC | Day | Parameter | mg/L | 2 | FALSE |  |  |  |  | 03726
Note on E7: Select from: Day 4 Hours Hour 30 Minutes 15 Minutes 5 Minutes Minute
Note on F7: Select From: Parameter Text Parameter Calculated
Note on H7: 0 will be used if left blank
Note on P7: Select from: Min Max Total Avg First Last Start Value End Value
Note on Q7: Interface. Enter minimum value to use as filter. Ie if 0 is entered, values<0 will be ignored when importing data.
Note on R7: Ie if 9999 is entered, values>9999 will be ignored when importing data.
Note on S7: Enter a value by which the imported data will be multiplied to convert it to the proper units. Leave it blank if no change is necessary.
Note on I7: Set to 1, TRUE, or Y if the Parameter should allow data qualifiers (<,>, or ND)
Note on C7: Scott Dorner: Location and Parameter Name will create the variable name (up to 40 characters)
Note on G7: 10 Characters Max
Note on D7: 20 Characters Max, combined with Short (C2)
Note on B2: Combined with Parameter Name to make Variable Name
Note on B3: Combined with Short Name to make Heading

## Clearwell
Location: | Clearwell | Area Name:
Location Name | CW |  |  |  |  | Location Desc
Short Location Name | CW
Desc: | Clearwell
Base Var # | 9000
| Parameter | Short |  |  |  | Dec | Allow |  | Entry | Entry | Description | Storet |  |  | Low | High | Scale
Var # | Name | Name | Frequency | Type | Units | Plcs | Symbol | Equation | Min | max | (Notes) | Code | Scada Tag | Statistic | Range | Range | Factor
1 | Flow | Flow | Day | Parameter | MGD | 3 | FALSE |  |  |  |  | 50050 |  | Avg
11 | Flow | Flow | Day | Parameter | gpm | 1 | FALSE |  |  |  |  | 00058 |  | Avg
21 | Total Suspended Solids | TSS | Day | Parameter | mg/l | 0 | FALSE |  |  |  |  | 00530 |  | Avg
31 | Hardness (CaCO3) | Hard | Day | Parameter | mg/l | 0 | FALSE |  |  |  |  | 00900 |  | Avg
41 | Alkalinity (CaCO3) | Alkal | Day | Parameter | mg/l | 2 | FALSE |  |  |  |  | 00410 |  | Avg
51 | Turbidity 15 Min | Turb | 15 Minutes | Parameter | NTU | 0 | FALSE |  |  |  |  | 82078 |  | Avg
61 | Turbidity | Turb | Day | Parameter | NTU | 0 | FALSE |  |  |  |  | 82078 |  | Avg
71 | Turbidity Hrly | Turb | Hour | Parameter | NTU | 0 | FALSE |  |  |  |  | 82078 |  | Avg
81 | Dissolved Oxygen | DO | Day | Parameter | mg/L | 2 | TRUE |  |  |  |  | 00300 |  | Avg
91 | Carbon Dioxide | CO2 | Day | Parameter | mg/L | 2 | TRUE |  |  |  |  | 00405 |  | Avg
101 | Aluminum | Al | Day | Parameter | ug/l | 2 | TRUE |  |  |  |  | 01105 |  | Avg
111 | Arsenic | As | Day | Parameter | ug/l | 0 | TRUE |  |  |  |  | 01002 |  | Avg
121 | Chloride | Cl | Day | Parameter | mg/l | 2 | TRUE |  |  |  |  | 00940 |  | Avg
131 | Chlorine Residual Max | Cl2 Max | Day | Parameter | mg/L | 2 | FALSE |  |  |  |  | 50060 |  | Max
141 | Chlorine Residual Min | Cl2 Min | Day | Parameter | mg/L | 2 | FALSE |  |  |  |  | 50060 |  | Min
151 | Chlorine Residual Avg | Cl2 Avg | Day | Parameter | mg/L | 2 | FALSE |  |  |  |  | 50060 |  | Avg
161 | Color | Color | Day | Parameter | ColorUnits | 0 | FALSE |  |  |  |  | 00079 |  | Avg
171 | Copper | Cu | Day | Parameter | ug/l | 0 | TRUE |  |  |  |  | 01042 |  | Avg
181 | Corrosivity | Corros | Day | Parameter | WtrNum | 0 | FALSE |  |  |  |  | 71814 |  | Avg
191 | Fluoride | F- | Day | Parameter | mg/l | 3 | TRUE |  |  |  |  | 00951 |  | Avg
201 | Foaming Agents | Foam | Day | Parameter | mg/l | 2 | FALSE |  |  |  |  | 01288 |  | Avg
211 | Iron | Fe | Day | Parameter | ug/l | 0 | TRUE |  |  |  |  | 01045 |  | Avg
221 | Lead | Pb | Day | Parameter | ug/l | 0 | TRUE |  |  |  |  | 01051 |  | Avg
231 | Manganese | Mn | Day | Parameter | ug/l | 0 | TRUE |  |  |  |  | 01055 |  | Avg
241 | Nitrate/Nitrite | NO 3/2 | Day | Parameter | mg/l | 2 | TRUE |  |  |  |  | 00630 |  | Avg
251 | Odor | Odor | Day | Parameter | Code | 0 | FALSE |  |  |  |  | 34773 |  | Avg
261 | Silver | Ag | Day | Parameter | ug/l | 0 | TRUE |  |  |  |  | 01077 |  | Avg
271 | Sulfate | SO4 | Day | Parameter | mg/l | 3 | TRUE |  |  |  |  | 00945 |  | Avg
281 | Total Dissolved Solids | TDS | Day | Parameter | mg/l | 2 | TRUE |  |  |  |  | 47004 |  | Avg
291 | Zinc | Zn | Day | Parameter | ug/l | 0 | TRUE |  |  |  |  | 01092 |  | Avg
301 | pH | pH | Day | Parameter | SU | 1 | FALSE |  |  |  |  | 00400 |  | Avg
311 | Temperature | Temp | Day | Parameter | Deg F | 0 | FALSE |  |  |  |  | 00011 |  | Avg
321 | Temperature | Temp | Day | Parameter | Deg C | 0 | FALSE |  |  |  |  | 00010 |  | Avg
331 | Run Time | Run Time | Day | Parameter | hrs | 1 | FALSE | [6 empty] | Avg
341 | Pumping Level | Pump Lvl | Day | Parameter | ft | 1 | FALSE | [6 empty] | Avg
351 | Static Level | Static Lvl | Day | Parameter | ft | 1 | FALSE | [6 empty] | Avg
361 | Hours at Rest | Hrs Rest | Day | Parameter | hrs | 2 | FALSE | [6 empty] | Avg
371 | Zeta Potential | Zeta | Day | Parameter | mV | 0 | FALSE | [6 empty] | Avg
381 | Power | Pwr | Day | Parameter | kwH | 2 | FALSE | [6 empty] | Avg
391 | Average Level | AvgLvl | Day | Parameter | ft | 1 | FALSE | [6 empty] | Avg
401 | Minimum Level | MinLvl | Day | Parameter | ft | 1 | FALSE | [6 empty] | Avg
411 | Maximum Level | MaxLvl | Day | Parameter | ft | 1 | FALSE | [6 empty] | Avg
421 | Average Pressure | AvgPress | Day | Parameter | psi | 0 | FALSE | [6 empty] | Avg
431 | Minimum Pressure | MinPress | Day | Parameter | psi | 0 | FALSE | [6 empty] | Avg
441 | Maximum Pressure | MaxPress | Day | Parameter | psi | 0 | FALSE | [6 empty] | Avg
451 | Segment Volume | Vol | Day | Calculated | MG | 1 | FALSE
461 | T10 | T10 | Day | Calculated | Mins | 1 | FALSE | ((Segment Vol (MG) / Flow (MGD) ) *24 * 60) * Baffling Factor
471 | CT Achieved | CT Achvd | Day | Calculated | mg/L - mins | 1 | FALSE | CL2 Residual (mg/L) * T10 (mins)
481 | 3 Log Giardia CT Required | 3L CT Req | Day | Calculated | mg/L - mins | 1 | FALSE | Final Temperature, pH, CL2
491 | 4 Log Viruses CT Required | 4 Log CT Req | Day | Calculated | mg/L - mins | 1 | FALSE | Table for Inactivation of viruses
501 | 3 Log Giardia CT Ratio | 3 Log CT Ratio | Day | Calculated | Ratio | 1 | FALSE | CT Achieved / 3 Log Giardia CT Required
511 | 4 Log Viruses CT Ratio | 4 Log CT Ratio | Day | Calculated | Ratio | 1 | FALSE | CT Achieved / 4 Log CT Required
521 | Giardia Log Inactivation | Gia Inact | Day | Calculated | Units | 1 | FALSE | 3 * 3 Log Giardia CT Ratio
531 | Viruses Log Inactivation |  | Day | Calculated | Units | 1 | FALSE | 3 * 4 Log Viruses Ratio
Note on E7: Select from: Day 4 Hours Hour 30 Minutes 15 Minutes 5 Minutes Minute
Note on F7: Select From: Parameter Text Parameter Calculated
Note on H7: 0 will be used if left blank
Note on P7: Select from: Min Max Total Avg First Last Start Value End Value
Note on Q7: Interface. Enter minimum value to use as filter. Ie if 0 is entered, values<0 will be ignored when importing data.
Note on R7: Ie if 9999 is entered, values>9999 will be ignored when importing data.
Note on S7: Enter a value by which the imported data will be multiplied to convert it to the proper units. Leave it blank if no change is necessary.
Note on I7: Set to 1, TRUE, or Y if the Parameter should allow data qualifiers (<,>, or ND)
Note on C7: Scott Dorner: Location and Parameter Name will create the variable name (up to 40 characters)
Note on G7: 10 Characters Max
Note on D7: 20 Characters Max, combined with Short (C2)
Note on B2: Combined with Parameter Name to make Variable Name
Note on B3: Combined with Short Name to make Heading

## Dist Monitoring
Location: | See Cell V8 to list multiple sites | MULTISITE | [16 empty] | 22 | 23 | 24 | 25 | 26
Location Name
Short Location Name
Desc:
Base Var #
Interface Settings
| Parameter | Short |  |  |  | Dec | Allow |  | Entry Min | Entry Max | Description | Storet |  |  | Low | High | Scale
Var # | Name | Name | Frequency | Type | Units | Plcs | Symbol | Equation |  |  | (Notes) | Code | Signal Tag | Statistic | Range | Range | Factor |  | Location: | Location Name | Short Location Name | Location Desc: | Base Var # | Area
1 | Coliform, Total |  | Daily | Text Parameter | P/A | 0 | FALSE | Absent,Present |  | 1.5 | Naturally present in the environment | 84382 | [5 empty] | 1 | DS1 | DS1 | DS1 | Distribution Site 1 | 30000 | Dist North | 119 | 3427 Colonel Vanderhorst | Dunes West- 2nd Right Off of Main Drag
11 | Coliform, Total |  | Daily | Parameter | #/100ml | 0 | TRUE |  |  |  |  | 84382 | [5 empty] | 1 | DS1U | DS1U | DS1U | Distribution Site 1 Upstream | 31000 | Dist North | 120 | 2896 Parkers Island Road | Hwy.41- 1rst Left Past Mattie
21 | E Coli |  | Daily | Parameter | #/100ml | 0 | TRUE |  |  |  |  | ECOLI | [5 empty] | 1 | DS1D | DS1D | DS1D | Distribution Site 1 Downstream | 32000 | Dist North | 121 | 2518 Willington Court | Dunes West- Off of Col. Vanderhorst
31 | Total Chlorine Residual | TRC | Daily | Parameter | mg/L | 2 | TRUE |  |  |  |  | 49153 | [5 empty] | 2 | DS2 | DS2 | DS2 | Distribution Site 2 | 33000 | Dist North | 122 | 2818 N Hwy.17 (AME Goodwill) | Hwy.41&17
41 | HPC |  | Daily | Parameter | cfu/mL | 1 | TRUE |  |  | 500 | Heterotrophic Plate Count (HPC, Method 9215C) formerly known as the standard plate count is used for estimating the number of live heterotropic bacteria in water samples. | 78943 | [5 empty] | 2 | DS2U | DS2U | DS2U | Distribution Site 2 Upstream | 34000 | Dist North | 123 | Longpoint Baptist Church | Next to Long Point Subdivision on Snowden Road
51 | Temperature | Temp | Daily | Parameter | Deg C | 1 | FALSE |  | 3 | 35 |  | 00010 | [5 empty] | 2 | DS2D | DS2D | DS2D | Distribution Site 2 Downstream | 35000 | Dist North | 124 | 606 Hidden Blvd. | Hidden Cove Off Long Point Road (Close To Ports)
61 | pH |  | Daily | Parameter | SU | 2 | FALSE |  | 6 | 9 |  | 00400 | [12 empty] | 125 | 1510 Wren Street | Cassina Heights
71 | Alkalinity (CaCO3) | Alkal | Day | Parameter | mg/L | 2 | TRUE |  |  |  | Water Quality Parameter (taken when Action Level (AL) of Lead or Copper is exceeded) | 00410 | [12 empty] | 126 | 1145 Six Mile Road | Six Mile Road ECCO
81 | Calcium |  | Day | Parameter | mg/L | 1 | TRUE |  |  |  | Water Quality Parameter (taken when Action Level (AL) of Lead or Copper is exceeded) | 00910 | [12 empty] | 127 | 1666 Snowden Road | In Snowden
91 | Orthophosphate | Ortho-P | Day | Parameter | mg/L | 1 | TRUE |  |  |  | Water Quality Parameter (taken when Action Level (AL) of Lead or Copper is exceeded) | 00660 | [12 empty] | 129 | 2235 Hugh Smith Court | Dunes West- 2nd Right Off of Pignatelli
101 | Silica |  | Day | Parameter | mg/L | 1 | TRUE |  |  |  | Water Quality Parameter (taken when Action Level (AL) of Lead or Copper is exceeded) | 00596 | [12 empty] | 130 | 2007 Presidio Drive | Quail Hollow on RRR Across From Raven's Run
[25 empty] | 131 | 2109 Williams Veneer | Dunes West Off Cotton Field
[25 empty] | 132 | 1239 Haig Lane | Charleston National- Off of Heathland Drive
[25 empty] | 133 | 3133 Ball Court | Dunes West Off of Cherokee Rose
[25 empty] | 134 | 3170 Pignatelli Crescent | Dunes West 2nd Left Past Harpers Ferry Way
[25 empty] | 135 | 287 Copahee Road | 5th Left Off of Hobcaw Drive in Hobcaw
[25 empty] | 136 | 2072 Lewisfield Court | Long Point Subdivision Off Rice Hope Past Seewee
[25 empty] | 137 | 2187 Andover Way | Park West Off of Park West Blvd.
[25 empty] | 138 | 2356 South Salt Wind Way | 2nd Left in Rivertown
[25 empty] | 139 | 394 Fern House Walk | Belle Hall 1rst Right Then Right Again
[25 empty] | 140 | 108 Historic Drive | Belle Hall Left on Veranda Then
[25 empty] | 141 | 701 Tybee Pass | Brickyard Right On Bridge, Right Gaston Gate Left Albercon
[25 empty] | 142 | Oakpoint Landing | Long Point Subdivision left on Enclave Dr. Then Right
[25 empty] | 143 | 4626 Cape Island Drive | Guerens Bridge-Woodville-Paradise Road
[25 empty] | 144 | 3008 Hwy.17N | Tire and Auto
[25 empty] | 145 | 1418 Tarrington Lane | RRR past 6 Mile (Murry's Uncle)
[25 empty] | 146 | 1096 Bee Hive Road | 10 Mile- 2nd Right Past BEC
[25 empty] | 147 | 1132 Yough Hall Road | Hwy.17 3rd Right Past BEC
[25 empty] | 148 | 3550 Woodspring | Commonwealth Turn Onto Deer Creek Road
[25 empty] | 149 | Iron Bridge Rd. Hwy. Dept.
[25 empty] | 150 | 1038 Theodore Road | Hwy.17N- Past BEC
[25 empty] | 151 | 3718 Zacoma | 1rst Right in Copahee
[25 empty] | 152 | Cario School | Parkwest
[25 empty] | 153 | Pickney School | Parkwest
[25 empty] | 154 | 1721 Bowline Drive | Dunes West; Off Ayers Way on Fountain Head
[25 empty] | 155 | 2818 Oak Manor | Dunes West; Off Ayers Way- 2nd Left
[25 empty] | 156 | 3009 Ashburton Way | Parkwest- End of Greymarsh
[25 empty] | 157 | 1933 Hubbell Drive | Park West; End of Greymarsh
[25 empty] | 158 | 2271 Captain Waring Court | Dunes West- Off Col. Vanderhorst
[25 empty] | 159 | 2085 Kings Gate Lane | Across From Planters Point Off Hwy. 41
[25 empty] | 160 | 1508 Red Drum Road | Rivertown Country Club; At the end
Note on B2: Combined with Parameter Name to make Variable Name
Note on B3: Combined with Short Name to make Heading
Note on C7: Scott Dorner: Location and Parameter Name will create the variable name (up to 40 characters)
Note on D7: 20 Characters Max, combined with Short (C2)
Note on E7: Select from: OPS 32 Day Hour 15 Minute OPS SQL Day 4 Hours Hour 30 Minutes 15 Minutes 5 Minutes Minute
Note on F7: Select From: Parameter Text Parameter Calculated
Note on G7: 10 Characters Max
Note on H7: 0 will be used if left blank
Note on I7: Set to 1, TRUE, or Y if the Parameter should allow data qualifiers (<,>, or ND)
Note on K7: Entry Min and Max sets warning limits when entering data for the variable. When entering data, if a value is entered outside of the range a warning message will be displayed and the user will be asked if they want to keep or discard the entry.
Note on P7: Select from: Min Max Total Avg First Last Start Value End Value
Note on Q7: Interface. Enter minimum value to use as filter. Ie if 0 is entered, values<0 will be ignored when importing data.
Note on R7: Ie if 9999 is entered, values>9999 will be ignored when importing data.
Note on S7: Enter a value by which the imported data will be multiplied to convert it to the proper units. Leave it blank if no change is necessary.
Note on W8: Combined with Parameter Name to make Variable Name
Note on X8: Combined with Short Name to make Heading

## Dist Disinfection Summary
Location: | Dist | Area Name:
Location Name | Dist
Short Location Name | Dist
Desc: | Distribution
Base Var # | 10000
Interface Settings
| Parameter | Short |  |  |  | Dec | Allow |  | Entry | Entry | Description | Storet |  |  | Low | High | Scale
Var # | Name | Name | Frequency | Type | Units | Plcs | Symbol | Equation | Min | max | (Notes) | Code | Signal Tag | Statistic | Range | Range | Factor
1 | Sites Residual Measured | Sites Resid | Daily | Calculated | Count | 0 |  | MVGT(-1, C10101,C10201,C10301) |  |  |  | 50600
11 | Cl2 Resid Avg | Cl2 Avg | Daily | Calculated | mg/L | 2 |  | MVAVG(C10101,C10201,C10301) |  |  |  | 78943
15 | Sites Disinfect NM HPC Meas | D NM HPC M | Daily | Calculated | Count | 0 |  | IF(ISBLANK(C10101) and NOT ISBLANK(C10111),1,0) + IF(ISBLANK(C10201) and NOT ISBLANK(C10211),1,0) + IF(ISBLANK(C10301) and NOT ISBLANK(C10311),1,0) |  |  |  | 49153
21 | Sites Disinfect ND & NO HPC 1 | D ND & NO HPC | Daily | Calculated | Count | 0 |  | IF(C10101= 0 and ISBLANK(C10111),1,0) + IF(C10201= 0 and ISBLANK(C10211),1,0) + IF(C10301= 0 and ISBLANK(C10311),1,0) |  |  |  | 50600
31 | Sites Disinfect ND & HPC >500 | D ND,HPC>500 | Daily | Calculated | Count | 0 |  | IF(C10101= 0 and C10111>500,1,0) + IF(C10201= 0 and C10211>500,1,0) |  |  |  | 78943
41 | Sites Disinfect NM & HPC >500 | D NM, HPC>500 | Daily | Calculated | Count | 0 |  | IF(ISBLANK(C10101) and C10111>500,1,0) + IF(ISBLANK(C10201) and C10211>500,1,0) |  |  |  | 49153
51 | Sites Total Coliform Samples Taken | TC Samples | Daily | Calculated | Count | 0 | FALSE | MVGT(-1,GETVAL(V9005),GETVAL(V9015)...) 'Must use GetVal when referring to a TextValue, list all your Dist Total Coliform Varaibles
54 | Sites Total Coliform Positive | TC Positive | Daily | Calculated | Count | 0 | FALSE | MVGT(1.1,GETVAL(V9005),GETVAL(V9015)...) 'Must use GetVal when referring to a TextValue, list all your Dist Total Coliform Varaibles, >1.1 works if list is setup Absent, Present (ie Absent will then =1, Present =2)
57 | Sites Total Coliform % Positive | TC % Positive | Daily | Calculated | % | 1 | FALSE | MSUM(C10054)/MSUM(C10051) * 100
101 | Site 1 Cl2 | Cl2 | Daily | Parameter | mg/L | 2 | [5 empty] | 50600
111 | Site 1 HPC | HPC | Daily | Parameter | cfu/mL | 1 |  |  |  |  | Heterotrophic Plate Count (HPC, Method 9215C) formerly known as the standard plate count is used for estimating the number of live heterotropic bacteria in water samples. | 78943
121 | Site 1 TDS | TDS | Daily | Parameter | mg/L | 0 | [5 empty] | 49153
201 | Site 2 Cl2 | Cl2 | Daily | Parameter | mg/L | 2 | [5 empty] | 50600
211 | Site 2 HPC | HPC | Daily | Parameter | cfu/mL | 1 |  |  |  |  | Heterotrophic Plate Count (HPC, Method 9215C) formerly known as the standard plate count is used for estimating the number of live heterotropic bacteria in water samples. | 78943
221 | Site 2 TDS | TDS | Daily | Parameter | mg/L | 0 | [5 empty] | 49153
Note on C7: Scott Dorner: Location and Parameter Name will create the variable name (up to 40 characters)
Note on D7: 20 Characters Max, combined with Short (C2)
Note on E7: Select from: OPS 32 Day Hour 15 Minute OPS SQL Day 4 Hours Hour 30 Minutes 15 Minutes 5 Minutes Minute
Note on F7: Select From: Parameter Text Parameter Calculated
Note on G7: 10 Characters Max
Note on H7: 0 will be used if left blank
Note on I7: Set to 1, TRUE, or Y if the Parameter should allow data qualifiers (<,>, or ND)
Note on P7: Select from: Min Max Total Avg First Last Start Value End Value
Note on Q7: Interface. Enter minimum value to use as filter. Ie if 0 is entered, values<0 will be ignored when importing data.
Note on R7: Ie if 9999 is entered, values>9999 will be ignored when importing data.
Note on S7: Enter a value by which the imported data will be multiplied to convert it to the proper units. Leave it blank if no change is necessary.
Note on B2: Combined with Parameter Name to make Variable Name
Note on B3: Combined with Short Name to make Heading

## Lead&Copper
Location: | See Cell V8 to list multiple sites | MULTISITE
Location Name | x | [23 empty] | Establishes action level (AL) of 0.015 mg/L for Pb and 1.3 mg/L for Cu based on
Short Location Name | x | [23 empty] | 90th percentile level of tap water samples. An AL exceedance is not a violation but
Desc: | x | [17 empty] | List each Lead and Copper site below. | [5 empty] | can trigger other requirements that include water quality parameter (WQP)
Base Var # | [18 empty] | Based on Lead and Copper Rule and Size of system you should have between 20 and 100 sites | [5 empty] | monitoring, corrosion control treatment (CCT), source water monitoring/treatment,
[13 empty] | Interface Settings | [5 empty] | See Lead and Copper Rule Quick Reference Guide for more info. | [5 empty] | public education, and lead service line replacement (LSLR).
| Parameter | Short |  |  |  | Dec | Allow |  | Entry | Entry | Description | Storet |  |  | Low | High | Scale
Var # | Name | Name | Frequency | Type | Units | Plcs | Symbol | Equation | Min | max | (Notes) | Code | Signal Tag | Statistic | Range | Range | Factor |  | Location: | Location Name | Short Location Name | Location Desc: | Base Var # | Area
1 | Lead | Pb | Daily | Parameter | mg/L | 3 | TRUE |  |  | 0.015 | Corrosion of household plumbing systems; Erosion of natural deposits | 01051 | [5 empty] | 1 | LC1 | LC1 | LC1 | 545 Marsh Grass | 20000 | Lead and Copper
11 | Copper | Cu | Daily | Parameter | mg/L | 1 | TRUE |  |  | 1.3 | Corrosion of household plumbing systems; Erosion of natural deposits; Leaching from wood preservatives | 78943 | [5 empty] | 2 | LC2 | LC2 | LC2 | 273 Coinbow Circle | 20100 | Lead and Copper
21 | pH | pH | Day | Parameter | SU | 1 | FALSE |  | 5 | 10 | Water Quality Parameter (taken when Action Level (AL) of Lead or Copper is exceeded) | 00400 | [5 empty] | 3 | LC3 | LC3 | LC3 | Mathis Ferry Fuel Express | 20200 | Lead and Copper
31 | Alkalinity (CaCO3) | Alkal | Day | Parameter | mg/L | 2 | TRUE |  |  |  | Water Quality Parameter (taken when Action Level (AL) of Lead or Copper is exceeded) | 00410 | [5 empty] | 4 | LC4 | LC4 | LC4 | 4020 Peggy Rd | 20300 | Lead and Copper
41 | Calcium |  | Day | Parameter | mg/L | 1 | TRUE |  |  |  | Water Quality Parameter (taken when Action Level (AL) of Lead or Copper is exceeded) | 00910 | [5 empty] | 5 | LC5 | LC5 | LC5 | 2388 Manzano Loop | 20400 | Lead and Copper
51 | Temperature | Temp | Day | Parameter | Deg C | 1 | FALSE |  | 4 | 35 | Water Quality Parameter (taken when Action Level (AL) of Lead or Copper is exceeded) | 00010 | [5 empty] | 6 | LC6 | LC6 | LC6 | 544 Woodside Drive | 20500 | Lead and Copper
61 | Orthophosphate | Ortho-P | Day | Parameter | mg/L | 1 | TRUE |  |  |  | Water Quality Parameter (taken when Action Level (AL) of Lead or Copper is exceeded) | 00660 | [5 empty] | 7 | LC7 | LC7 | LC7 | 201 Appletree Drive | 20600 | Lead and Copper
71 | Silica |  | Day | Parameter | mg/L | 1 | TRUE |  |  |  | Water Quality Parameter (taken when Action Level (AL) of Lead or Copper is exceeded) | 00596 | [5 empty] | 8 | LC8 | LC8 | LC8 | 5645 Sage Brush | 20700 | Lead and Copper
[18 empty] | 9 | LC9 | LC9 | LC9 | 5442 Gila River | 20800 | Lead and Copper
[18 empty] | 10 | LC10 | LC10 | LC10 | 243 Bradley Rd | 20900 | Lead and Copper
[18 empty] | 11 | LC11 | LC11 | LC11 | 12 Tyler Street | 21000 | Lead and Copper
[18 empty] | 12 | LC12 | LC12 | LC12 | 6421 Main | 21100 | Lead and Copper
[18 empty] | 13 | LC13 | LC13 | LC13 | 2443 Zachary Drive | 21200 | Lead and Copper
[18 empty] | 14 | LC14 | LC14 | LC14 | 101 Sheridan Circle | 21300 | Lead and Copper
[18 empty] | 15 | LC15 | LC15 | LC15 | 5673 Ave J | 21400 | Lead and Copper
[18 empty] | 16 | LC16 | LC16 | LC16 | 9543 Lincoln | 21500 | Lead and Copper
[18 empty] | 17 | LC17 | LC17 | LC17 | 125 MLK Drive | 21600 | Lead and Copper
[18 empty] | 18 | LC18 | LC18 | LC18 | 175 Wiley Road | 21700 | Lead and Copper
[18 empty] | 19 | LC19 | LC19 | LC19 | 870 Enchanted Hills | 21800 | Lead and Copper
[18 empty] | 20 | LC20 | LC20 | LC20 | 7644 Hwy 528 | 21900 | Lead and Copper
Note on B2: Combined with Parameter Name to make Variable Name
Note on B3: Combined with Short Name to make Heading
Note on C7: Scott Dorner: Location and Parameter Name will create the variable name (up to 40 characters)
Note on D7: 20 Characters Max, combined with Short (C2)
Note on E7: Select from: OPS 32 Day Hour 15 Minute OPS SQL Day 4 Hours Hour 30 Minutes 15 Minutes 5 Minutes Minute
Note on F7: Select From: Parameter Text Parameter Calculated
Note on G7: 10 Characters Max
Note on H7: 0 will be used if left blank
Note on I7: Set to 1, TRUE, or Y if the Parameter should allow data qualifiers (<,>, or ND)
Note on P7: Select from: Min Max Total Avg First Last Start Value End Value
Note on Q7: Interface. Enter minimum value to use as filter. Ie if 0 is entered, values<0 will be ignored when importing data.
Note on R7: Ie if 9999 is entered, values>9999 will be ignored when importing data.
Note on S7: Enter a value by which the imported data will be multiplied to convert it to the proper units. Leave it blank if no change is necessary.
Note on W8: Combined with Parameter Name to make Variable Name
Note on X8: Combined with Short Name to make Heading

## Sandy LC
Location: | See Cell V8 to list multiple sites | MULTISITE
Location Name | x | [23 empty] | Establishes action level (AL) of 0.015 mg/L for Pb and 1.3 mg/L for Cu based on
Short Location Name | x | [23 empty] | 90th percentile level of tap water samples. An AL exceedance is not a violation but
Desc: | x | [17 empty] | List each Lead and Copper site below. | [5 empty] | can trigger other requirements that include water quality parameter (WQP)
Base Var # | [18 empty] | Based on Lead and Copper Rule and Size of system you should have between 20 and 100 sites | [5 empty] | monitoring, corrosion control treatment (CCT), source water monitoring/treatment,
[13 empty] | Interface Settings | [5 empty] | See Lead and Copper Rule Quick Reference Guide for more info. | [5 empty] | public education, and lead service line replacement (LSLR).
| Parameter | Short |  |  |  | Dec | Allow |  | Entry | Entry | Description | Storet |  |  | Low | High | Scale
Var # | Name | Name | Frequency | Type | Units | Plcs | Symbol | Equation | Min | max | (Notes) | Code | Signal Tag | Statistic | Range | Range | Factor |  | Location: | Location Name | Short Location Name | Location Desc: | Base Var # | Area
1 | Lead | Pb | Daily | Parameter | mg/L | 3 | TRUE |  |  | 0.015 | Corrosion of household plumbing systems; Erosion of natural deposits | 01051 | [5 empty] | 1 | LC1 | LC1 | LC1 | 545 Marsh Grass | 25000 | Distribution
11 | Copper | Cu | Daily | Parameter | mg/L | 1 | TRUE |  |  | 1.3 | Corrosion of household plumbing systems; Erosion of natural deposits; Leaching from wood preservatives | 01042 | [5 empty] | 2 | LC2 | LC2 | LC2 | 273 Coinbow Circle | 25100 | Distribution
[12 empty] | 00400 | [5 empty] | 3 | LC3 | LC3 | LC3 | Mathis Ferry Fuel Express | 25200 | Distribution
[12 empty] | 00410 | [5 empty] | 4 | LC4 | LC4 | LC4 | 4020 Peggy Rd | 25300 | Distribution
[12 empty] | 00910 | [5 empty] | 5 | LC5 | LC5 | LC5 | 2388 Manzano Loop | 25400 | Distribution
[12 empty] | 00010 | [5 empty] | 6 | LC6 | LC6 | LC6 | 544 Woodside Drive | 25500 | Distribution
[12 empty] | 00660 | [5 empty] | 7 | LC7 | LC7 | LC7 | 201 Appletree Drive | 25600 | Distribution
[12 empty] | 00596 | [5 empty] | 8 | LC8 | LC8 | LC8 | 5645 Sage Brush | 25700 | Distribution
[18 empty] | 9 | LC9 | LC9 | LC9 | 5442 Gila River | 25800 | Distribution
[18 empty] | 10 | LC10 | LC10 | LC10 | 243 Bradley Rd | 25900 | Distribution
[18 empty] | 11 | LC11 | LC11 | LC11 | 12 Tyler Street | 26000 | Distribution
[18 empty] | 12 | LC12 | LC12 | LC12 | 6421 Main | 26100 | Distribution
[18 empty] | 13 | LC13 | LC13 | LC13 | 2443 Zachary Drive | 26200 | Distribution
[18 empty] | 14 | LC14 | LC14 | LC14 | 101 Sheridan Circle | 26300 | Distribution
[18 empty] | 15 | LC15 | LC15 | LC15 | 5673 Ave J | 26400 | Distribution
[18 empty] | 16 | LC16 | LC16 | LC16 | 9543 Lincoln | 26500 | Distribution
[18 empty] | 17 | LC17 | LC17 | LC17 | 125 MLK Drive | 26600 | Distribution
[18 empty] | 18 | LC18 | LC18 | LC18 | 175 Wiley Road | 26700 | Distribution
[18 empty] | 19 | LC19 | LC19 | LC19 | 870 Enchanted Hills | 26800 | Distribution
[18 empty] | 20 | LC20 | LC20 | LC20 | 7644 Hwy 528 | 26900 | Distribution
Note on B2: Combined with Parameter Name to make Variable Name
Note on B3: Combined with Short Name to make Heading
Note on C7: Scott Dorner: Location and Parameter Name will create the variable name (up to 40 characters)
Note on D7: 20 Characters Max, combined with Short (C2)
Note on E7: Select from: OPS 32 Day Hour 15 Minute OPS SQL Day 4 Hours Hour 30 Minutes 15 Minutes 5 Minutes Minute
Note on F7: Select From: Parameter Text Parameter Calculated
Note on G7: 10 Characters Max
Note on H7: 0 will be used if left blank
Note on I7: Set to 1, TRUE, or Y if the Parameter should allow data qualifiers (<,>, or ND)
Note on P7: Select from: Min Max Total Avg First Last Start Value End Value
Note on Q7: Interface. Enter minimum value to use as filter. Ie if 0 is entered, values<0 will be ignored when importing data.
Note on R7: Ie if 9999 is entered, values>9999 will be ignored when importing data.
Note on S7: Enter a value by which the imported data will be multiplied to convert it to the proper units. Leave it blank if no change is necessary.
Note on W8: Combined with Parameter Name to make Variable Name
Note on X8: Combined with Short Name to make Heading

## Well
Location: | Well 1 | Area Name:
Location Name | W01
Short Location Name | W01
Desc: | Well #1
Base Var # | 15000
Interface Settings
| Parameter | Short |  |  |  | Dec | Allow |  | Entry | Entry | Description | Storet |  |  | Low | High | Scale
Var # | Name | Name | Frequency | Type | Units | Plcs | Symbol | Equation | Min | max | (Notes) | Code | Signal Tag | Statistic | Range | Range | Factor
1 | Flow Meter | Flow Mtr | Daily | Parameter | Gallons | 0 | FALSE
11 | Flow | Flow | Daily | Parameter | MGD | 2 | FALSE | DDIF(15001) |  |  | Make calc if based on meter var | 50050
21 | Power Meter | Pwr Mtr | Daily | Parameter | KWH | 0 | FALSE
22 | Power Used | Pwr Used | Daily | Calculated | KWH | 0 | FALSE | DDIF(C15021)
31 | Run Time Meter | RT Mtr | Daily | Parameter | Hours | 0 | FALSE
32 | Run Time | Runtime | Daily | Parameter | Hours | 0 | FALSE | DDIF(C15031)
36 | Motor Starts Meter | Well Starts Met | Daily | Parameter | Starts | 0
37 | Motor Starts Total | Well Starts Tot | Daily | Calculated | Starts | 0 |  | DDIF(V15036)
41 | Pressure | Pressure | Daily | Parameter | PSI | 1 | FALSE
42 | Discharge Pressure Min | Disch psi Min | Daily | Parameter | PSI | 1 | FALSE
43 | Discharge Pressure Max | Disch psi Max | Daily | Parameter | PSI | 1 | FALSE
44 | Discharge Pressure Avg | Disch psi Avg | Daily | Parameter | PSI | 1 | FALSE
51 | pH | pH | Daily | Parameter | SU | 1 | FALSE |  |  |  |  | 00400
61 | Temperature | Temp | Daily | Parameter | Deg F | 1 | FALSE |  |  |  |  | 00011
71 | Chromium 6 | Cr6 | Daily | Prameter | mg/L | 3 | FALSE |  |  |  |  | 49153
81 | Fecal | Fecal | Daily | Parameter | #/100ml | 0 | FALSE |  |  |  |  | 50600
83 | Bacti | Bacti | Daily | Parameter | #/100ml | 0 | FALSE |  |  |  |  | 78943
85 | HPC | HPC | Daily | Parameter | cfu/mL | 0 | FALSE |  |  |  | Heterotrophic Plate Count (HPC, Method 9215C) formerly known as the standard plate count is used for estimating the number of live heterotropic bacteria in water samples. | 49153
Note on C7: Scott Dorner: Location and Parameter Name will create the variable name (up to 40 characters)
Note on D7: 20 Characters Max, combined with Short (C2)
Note on E7: Select from: OPS 32 Day Hour 15 Minute OPS SQL Day 4 Hours Hour 30 Minutes 15 Minutes 5 Minutes Minute
Note on F7: Select From: Parameter Text Parameter Calculated
Note on G7: 10 Characters Max
Note on H7: 0 will be used if left blank
Note on I7: Set to 1, TRUE, or Y if the Parameter should allow data qualifiers (<,>, or ND)
Note on P7: Select from: Min Max Total Avg First Last Start Value End Value
Note on Q7: Interface. Enter minimum value to use as filter. Ie if 0 is entered, values<0 will be ignored when importing data.
Note on R7: Ie if 9999 is entered, values>9999 will be ignored when importing data.
Note on S7: Enter a value by which the imported data will be multiplied to convert it to the proper units. Leave it blank if no change is necessary.
Note on B2: Combined with Parameter Name to make Variable Name
Note on B3: Combined with Short Name to make Heading

## CCR
Location: | CCR | Area Name:
Location Name | CCR
Short Location Name | [7 empty] | 1000000000
Desc: | CCR Variables | [6 empty] | 5e-09
Base Var # | 20000 | [6 empty] | 5
[10 empty] | For CCR we enter the MCL in Entry Max |  |  | Interface Settings
| Parameter | Short |  |  |  | Dec | Allow |  | Entry | Entry | Description | Storet |  |  | Low | High | Scale | UD3 | UD4 (MCLG)
Var # | Name | Name | Frequency | Type | Units | Plcs | Symbol | Equation | Min | max | (Notes) | Code | Signal Tag | Statistic | Range | Range | Factor
1 | Total Coliform |  | Daily | Text Parameter | P/A | 0 | FALSE |  |  |  | Naturally present in the environment | 84382 | [5 empty] | Microbiological Contaminants | 0
2 | Total Coliform Monthly % Pos |  | Daily | Calculated | % | 0 | FALSE |  |  | 5 | Naturally present in the environment | 84382 | [5 empty] | Microbiological Contaminants | 0 | Note: MCL is 5% are positive
11 | Fecal Coliform |  | Daily | Parameter | P/A | 0 | FALSE |  |  |  | Human and animal fecal waste | 31611 | [5 empty] | Microbiological Contaminants
13 | E. Coli |  | Daily | Parameter | P/A | 0 | FALSE |  |  |  | Human and animal fecal waste | 31648 | [5 empty] | Microbiological Contaminants
15 | Total Organic Carbon |  | Daily | Parameter | mg/L | 0 | FALSE |  |  |  | Naturally present in the environment | 03726 | [5 empty] | Microbiological Contaminants
17 | Turbidity |  | Daily | Parameter | NTU | 2 | FALSE |  |  |  | Soil runoff | 45626 | [5 empty] | Microbiological Contaminants |  | Note: This is your Filtered Water Turbidity (you should already have a var for this)
19 | Beta/photon emitters |  | Daily | Parameter | mrem/yr | 0 | TRUE |  |  | 4 | Decay of natural and man-made deposits | 03501 | [5 empty] | Radioactive Contaminants | 0
21 | Alpha emitters |  | Daily | Parameter | pCi/L | 0 | TRUE |  |  | 15 | Erosion of natural deposits | 00149 | [5 empty] | Radioactive Contaminants | 0
23 | Combined radium |  | Daily | Parameter | pCi/L | 0 | TRUE |  |  | 5 | Erosion of natural deposits | 09501 | [5 empty] | Radioactive Contaminants | 0
25 | Uranium |  | Daily | Parameter | ug/L | 1 | TRUE |  |  | 30 | Erosion of natural deposits | 22601 | [5 empty] | Radioactive Contaminants | 0
27 | Antimony |  | Daily | Parameter | ppb | 1 | TRUE |  |  | 6 | Discharge from petroleum refineries; fire retardants; ceramics; electronics; solder | 01097 | [5 empty] | Inorganic Contaminants | 6
29 | Arsenic |  | Daily | Parameter | ppb | 1 | TRUE |  |  | 10 | Erosion of natural deposits; Runoff from orchards; Runoff from glass and electronics production wastes | 01002 | [5 empty] | Inorganic Contaminants | 0
31 | Asbestos |  | Daily | Parameter | MFL | 1 | TRUE |  |  | 7 | Decay of asbestos cement water mains; Erosion of natural deposits | 81855 | [5 empty] | Inorganic Contaminants | 7
33 | Barium |  | Daily | Parameter | ppm | 2 | TRUE |  |  | 2 | Discharge of drilling wastes; Discharge from metal refineries; Erosion of natural deposits | 01007 | [5 empty] | Inorganic Contaminants | 2
35 | Beryllium |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 4 | Discharge from metal refineries and coal-burning factories; Discharge from electrical, aerospace, and defense industries | 01012 | [5 empty] | Inorganic Contaminants | 4
37 | Bromate |  | Daily | Prameter | ppb | 3 | TRUE |  |  | 10 | By-product of drinking water disinfection | BROMATE | [5 empty] | Inorganic Contaminants | 0
39 | Cadmium |  | Daily | Parameter | ppbn | 2 | TRUE |  |  | 5 | Corrosion of galvanized pipes; Erosion of natural deposits; Discharge from metal refineries; Runoff from waste batteries and paints | 01027 | [5 empty] | Inorganic Contaminants | 5
41 | Chloramines |  | Daily | Parameter | ppm | 0 | TRUE |  |  | 4 | Water additive used to control microbes | CLMINES | [5 empty] | Inorganic Contaminants | 4
43 | Chlorine |  | Daily | Parameter | ppm | 1 | TRUE |  |  | 4 | Water additive used to control microbes | 50064 | [5 empty] | Inorganic Contaminants | 4
45 | Chromium |  | Daily | Parameter | ppb | 1 | TRUE |  |  | 100 | Discharge from steel and pulp mills; Erosion of natural deposits | 01034 | [5 empty] | Inorganic Contaminants | 800
47 | Chlorite |  | Daily | Parameter | ppm | 2 | TRUE |  |  | 1 | By-product of drinking water disinfection | CHLORITE | [5 empty] | Inorganic Contaminants | 0.8
49 | Chlorine Dioxide |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 800 | Water additive used to control microbes | CL2O2 | [5 empty] | Inorganic Contaminants | 100
51 | Copper |  | Daily | Parameter | ppm | 2 | TRUE |  |  | 1.3 | Corrosion of household plumbing systems; Erosion of natural deposits; Leaching from wood preservatives | 01042 | [5 empty] | Inorganic Contaminants | 1.3
53 | Cyanide |  | Daily | Parameter | ppb | 0 | TRUE |  |  | 200 | Discharge from steel/metal factories; Discharge from plastic and fertilizer factories | 00720 | [5 empty] | Inorganic Contaminants | 200
55 | Fluoride |  | Daily | Parameter | ppm | 2 | TRUE |  |  | 4 | Erosion of natural deposits; Water additive which promotes strong teeth; Discharge from fertilizer and aluminum factories | 00951 | [5 empty] | Inorganic Contaminants | 4
57 | Lead |  | Daily | Parameter | ppb | 1 | TRUE |  |  | 15 | Corrosion of household plumbing systems; Erosion of natural deposits | 01051 | [5 empty] | Inorganic Contaminants | 0
59 | Mercury |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 2 | Erosion of natural deposits; Discharge from refineries and factories; Runoff from landfills; Runoff from cropland | 71900 | [5 empty] | Inorganic Contaminants | 2
61 | Nitrate |  | Daily | Parameter | ppb | 1 | TRUE |  |  | 10 | Runoff from fertilizer use; Leaching from septic tanks, sewage; Erosion of natural deposits | 00620 | [5 empty] | Inorganic Contaminants | 10
63 | Nitrite |  | Daily | Parameter | ppb | 1 | TRUE |  |  | 1 | Runoff from fertilizer use; Leaching from septic tanks, sewage; Erosion of natural deposits | 00615 | [5 empty] | Inorganic Contaminants | 1
65 | Selenium |  | Daily | Parameter | ppb | 1 | TRUE |  |  | 50 | Discharge from petroleum and metal refineries; Erosion of natural deposits; Discharge from mines | 01147 | [5 empty] | Inorganic Contaminants | 50
67 | Thallium |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 2 | Leaching from ore-processing sites; Discharge from electronics, glass,and drug factories | 01059 | [5 empty] | Inorganic Contaminants | 0.5
69 | 2,4-D |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 70 | Runoff from herbicide used on row crops | 03757 | [5 empty] | Synthetic Organic Contaminants | 70
71 | 2,4,5-TP |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 50 | Residue of banned herbicide | 03614 | [5 empty] | Synthetic Organic Contaminants | 50
73 | Acrylamide |  | Daily | Parameter | ppb | 2 | TRUE |  |  |  | Added to water during sewage/wastewater treatment | 38576 | [5 empty] | Synthetic Organic Contaminants | 0
75 | Alachlor |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 2 | Runoff from herbicide used on row crops | 77825 | [5 empty] | Synthetic Organic Contaminants | 0
77 | Atzazine |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 3 | Runoff from herbicide used on row crops | ATZAZ | [5 empty] | Synthetic Organic Contaminants | 3
79 | Benzo(a)pyrene |  | Daily | Parameter | nanograms/L | 2 | TRUE |  |  | 200 | Leaching from linings of water storage tanks and distribution lines | 03648 | [5 empty] | Synthetic Organic Contaminants | 0
81 | Carbofuran |  | Daily | Parameter | ppb | 1 | TRUE |  |  | 40 | Leaching of soil fumigant used on rice and alfalfa | 81405 | [5 empty] | Synthetic Organic Contaminants | 40
83 | Chlordane |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 2 | Residue of banned termiticide | 03743 | [5 empty] | Synthetic Organic Contaminants | 0
85 | Dalapon |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 200 | Runoff from herbicide used on rights of way | 30200 | [5 empty] | Synthetic Organic Contaminants | 200
87 | Di(2-ethylhexyl)adipate |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 400 | Discharge from chemical factories | DIADIP | [5 empty] | Synthetic Organic Contaminants | 400
89 | Di(2-ethylhexyl)phthalate |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 6 | Discharge from rubber and chemical factories | DIPHTH | [5 empty] | Synthetic Organic Contaminants | 0
91 | Dibromochloropropane |  | Daily | Parameter | ppt | 2 | TRUE |  |  | 200 | Runoff/leaching from soil fumigant used on soybeans, cotton,pineapples, and orchards | 38437 | [5 empty] | Synthetic Organic Contaminants | 0
93 | Dinoseb |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 7 | Runoff from herbicide used on soybeans and vegetables | 30191 | [5 empty] | Synthetic Organic Contaminants | 7
95 | Diquat |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 20 | Runoff from herbicide use | 04443 | [5 empty] | Synthetic Organic Contaminants | 20
97 | Dioxin |  | Daily | Parameter | ppq | 0 | TRUE |  |  | 30 | Emissions from waste incineration and other combustion; Discharge from chemical factories | 03767 | [5 empty] | Synthetic Organic Contaminants | 0
99 | Endothall |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 100 | Runoff from herbicide use | 38926 | [5 empty] | Synthetic Organic Contaminants | 100
101 | Endrin |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 2 | Residue of banned insecticide | 39390 | [5 empty] | Synthetic Organic Contaminants | 2
103 | Epichlorohydrin |  | Daily | Parameter | ppb | 2 | TRUE |  |  |  | Discharge from industrial chemical factories; An impurity of some water treatment chemicals | 81679 | [5 empty] | Synthetic Organic Contaminants | 0
105 | Ethylene dibromide |  | Daily | Parameter | ppt | 0 | TRUE |  |  | 50 | Discharge from petroleum refineries | EDB | [5 empty] | Synthetic Organic Contaminants | 0
107 | Glyphosate |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 700 | Runoff from herbicide use | 79743 | [5 empty] | Synthetic Organic Contaminants | 700
109 | Heptachlor |  | Daily | Parameter | ppt | 0 | TRUE |  |  | 400 | Residue of banned insecticide | 39410 | [5 empty] | Synthetic Organic Contaminants | 0
111 | Heptachlor epoxide |  | Daily | Parameter | ppt | 0 | TRUE |  |  | 200 | Breakdown of heptachlor | 39420 | [5 empty] | Synthetic Organic Contaminants | 0
113 | Hexachlorobenzene |  | Daily | Parameter | ppb | 1 | TRUE |  |  | 1 | Discharge from metal refineries and agricultural chemical factories | 39700 | [5 empty] | Synthetic Organic Contaminants | 0
115 | Hexachlorocyclopent |  | Daily | Parameter | ppb | 1 | TRUE |  |  | 50 | Discharge from chemical factories | 78022 | [5 empty] | Synthetic Organic Contaminants | 50
117 | Lindane |  | Daily | Parameter | ppt | 0 | TRUE |  |  | 200 | Runoff/leaching from insecticide used on cattle, lumber, gardens | 39782 | [5 empty] | Synthetic Organic Contaminants | 200
119 | Methoxychlor |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 40 | Runoff/leaching from insecticide used on fruits, vegetables, alfalfa, livestock | 39480 | [5 empty] | Synthetic Organic Contaminants | 40
121 | Oxamyl |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 200 | Runoff/leaching from insecticide used on apples, potatoes and tomatoes | 38865 | [5 empty] | Synthetic Organic Contaminants | 200
123 | PCBs |  | Daily | Parameter | ppt | 0 | TRUE |  |  | 500 | Runoff from landfills; Discharge of waste chemicals | 39516 | [5 empty] | Synthetic Organic Contaminants | 0
125 | Pentachlorophenol |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 1 | Discharge from wood preserving factories | 39032 | [5 empty] | Synthetic Organic Contaminants | 0
127 | Picloram |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 500 | Herbicide runoff | 39720 | [5 empty] | Synthetic Organic Contaminants | 500
129 | Simazine |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 4 | Herbicide runoff | 39055 | [5 empty] | Synthetic Organic Contaminants | 4
131 | Toxaphene |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 3 | Runoff/leaching from insecticide used on cotton and cattle | 39400 | [5 empty] | Synthetic Organic Contaminants | 0
133 | Benzene |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 5 | Discharge from factories; Leaching from gas storage tanks and landfills | 61290 | [5 empty] | Volatile Organic Contaminants | 0
135 | Carbon tetrachloride |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 5 | Discharge from chemical plants and other industrial activities | 32102 | [5 empty] | Volatile Organic Contaminants | 0
137 | Chlorobenzene |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 100 | Discharge from chemical and agricultural chemical factories | 34301 | [5 empty] | Volatile Organic Contaminants | 100
139 | o-Dichlorobenzene |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 600 | Discharge from industrial chemical factories | 04150 | [5 empty] | Volatile Organic Contaminants | 600
141 | p-Dichlorobenzene |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 75 | Discharge from industrial chemical factories | pDCB | [5 empty] | Volatile Organic Contaminants | 75
143 | 1,2-Dichloroethane |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 5 | Discharge from industrial chemical factories | 32103 | [5 empty] | Volatile Organic Contaminants | 0
145 | 1,1-Dichloroethylene |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 7 | Discharge from industrial chemical factories | 34501 | [5 empty] | Volatile Organic Contaminants | 7
147 | cis-1,2-Dichloroethylene |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 70 | Discharge from industrial chemical factories | 77093 | [5 empty] | Volatile Organic Contaminants | 70
149 | trans-1,2-Dichloroethylene |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 100 | Discharge from industrial chemical factories | 1,2-DCE | [5 empty] | Volatile Organic Contaminants | 100
151 | Dichloromethane |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 5 | Discharge from pharmaceutical and chemical factories | DCM | [5 empty] | Volatile Organic Contaminants | 0
153 | 1,2-Dichloropropane |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 5 | Discharge from industrial chemical factories | 34541 | [5 empty] | Volatile Organic Contaminants | 0
155 | Ethylbenzene |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 700 | Discharge from petroleum refineries | 34371 | [5 empty] | Volatile Organic Contaminants | 700
157 | HAA5 |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 60 | By-product of drinking water disinfection | HAA5 | [5 empty] | Volatile Organic Contaminants
159 | Styrene |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 100 | Discharge from rubber and plastic factories; Leaching from landfills | 77128 | [5 empty] | Volatile Organic Contaminants | 100
161 | Tetrachloroethylene |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 5 | Discharge from factories and dry factories | 34475 | [5 empty] | Volatile Organic Contaminants | 0
163 | 1,2,4-Trichlorobenzene |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 70 | Discharge from textile-finishing factories | 03684 | [5 empty] | Volatile Organic Contaminants | 70
165 | 1,1,1-Trichloroethane |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 200 | Discharge from metal degreasing sites and other factories | 34506 | [5 empty] | Volatile Organic Contaminants | 200
167 | 1,1,2-Trichloroethane |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 5 | Discharge from industrial chemical factories | 34511 | [5 empty] | Volatile Organic Contaminants | 3
169 | Trichloroethylene |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 5 | Discharge from metal degreasing sites and other factories | 39180 | [5 empty] | Volatile Organic Contaminants | 0
171 | TTHMs |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 80 | By-product of drinking water disinfection | 82080 | [5 empty] | Volatile Organic Contaminants
173 | Toluene |  | Daily | Parameter | ppm | 2 | TRUE |  |  | 1 | Discharge from petroleum factories | 34010 | [5 empty] | Volatile Organic Contaminants | 1
175 | Vinyl Chloride |  | Daily | Parameter | ppb | 2 | TRUE |  |  | 2 | Leaching from PVC piping;Discharge from plastics factories | 39175 | [5 empty] | Volatile Organic Contaminants | 0
177 | Xylenes |  | Daily | Parameter | ppm | 2 | TRUE |  |  | 10 | Discharge from petroleum factories; Discharge from chemical factories | 81551 | [5 empty] | Volatile Organic Contaminants | 10 |  | 2
Note on B2: Combined with Parameter Name to make Variable Name
Note on B3: Combined with Short Name to make Heading
Note on C7: Scott Dorner: Location and Parameter Name will create the variable name (up to 40 characters)
Note on D7: 20 Characters Max, combined with Short (C2)
Note on E7: Select from: OPS 32 Day Hour 15 Minute OPS SQL Day 4 Hours Hour 30 Minutes 15 Minutes 5 Minutes Minute
Note on F7: Select From: Parameter Text Parameter Calculated
Note on G7: 10 Characters Max
Note on H7: 0 will be used if left blank
Note on I7: Set to 1, TRUE, or Y if the Parameter should allow data qualifiers (<,>, or ND)
Note on P7: Select from: Min Max Total Avg First Last Start Value End Value
Note on Q7: Interface. Enter minimum value to use as filter. Ie if 0 is entered, values<0 will be ignored when importing data.
Note on R7: Ie if 9999 is entered, values>9999 will be ignored when importing data.
Note on S7: Enter a value by which the imported data will be multiplied to convert it to the proper units. Leave it blank if no change is necessary.
Note on C9: Scott Dorner: Total Coliform is usually setup in the Dist Monitoring and should be removed from here

## Sheet1
Storet | Contaminant | Source | Health Effect
84382 | Total Coliform | Naturally present in the environment | Coliforms are bacteria that are naturally present in the environment and are used as an indicator that other, potentially-harmful, bacteria may be present. Coliforms were found in more samples than allowed and this was a warning of potential problems.
84382 | Total Coliform Monthly % Pos | Human and animal fecal waste | Fecal coliforms and E. coli are bacteria whose presence indicates that the water may be contaminated with human or animal wastes. Microbes in these wastes can cause shortterm effects, such as diarrhea, cramps, nausea, headaches, or other symptoms. They may pose a special health risk for infants, young children, and people with severelycompromised immune systems.
31611 | Fecal Coliform | Naturally present in the environment | Total organic carbon (TOC) has no health effects. However, total organic carbon provides a medium for the formation of disinfection byproducts. These byproducts include trihalomethanes (THMs) and haloacetic acids (HAAs). Drinking water containing these byproducts in excess of the MCL may lead to adverse health effects, liver, or kidney problems, or nervous system effects, and may lead to an increased risk of getting cancer.
31648 | E. Coli | Soil runoff | Turbidity has no health effects. However, turbidity can interfere with disinfection and provide a medium for microbial growth. Turbidity may indicate the presence of disease-causing organisms. These organisms include bacteria, viruses, and parasites that can cause symptoms such as nausea, cramps, diarrhea and associated headaches.
03726 | Total Organic Carbon | Naturally present in the environment | Certain minerals are radioactive and may emit forms of radiation known as photons and beta radiation. Some people who drink water containing beta and photon emitters in excess of the MCL over many years may have an increased risk of getting cancer.
45626 | Turbidity | Soil runoff | Certain minerals are radioactive and may emit a form of radiation known as alpha radiation. Some people who drink water containing alpha emitters in excess of the MCL over many years may have an increased risk of getting cancer.
03501 | Beta/photon emitters | Decay of natural and man-made deposits | Some people who drink water containing radium 226 or 228 in excess of the MCL over many years may have an increased risk of getting cancer.
00149 | Alpha emitters | Erosion of natural deposits | Some people who drink water containing uranium in excess of the MCL over many years may have an increased risk of getting cancer and kidney toxicity
09501 | Combined radium | Erosion of natural deposits
22601 | Uranium | Erosion of natural deposits
01097 | Antimony | Discharge from petroleum refineries; fire retardants; ceramics; electronics; solder
01002 | Arsenic | Erosion of natural deposits; Runoff from orchards; Runoff from glass and electronics production wastes
81855 | Asbestos | Decay of asbestos cement water mains; Erosion of natural deposits
01007 | Barium | Discharge of drilling wastes; Discharge from metal refineries; Erosion of natural deposits
01012 | Beryllium | Discharge from metal refineries and coal-burning factories; Discharge from electrical, aerospace, and defense industries
BROMATE | Bromate | By-product of drinking water disinfection
01027 | Cadmium | Corrosion of galvanized pipes; Erosion of natural deposits; Discharge from metal refineries; Runoff from waste batteries and paints
CLMINES | Chloramines | Water additive used to control microbes
50064 | Chlorine | Water additive used to control microbes
01034 | Chromium | Discharge from steel and pulp mills; Erosion of natural deposits
CHLORITE | Chlorite | By-product of drinking water disinfection
CL2O2 | Chlorine Dioxide | Water additive used to control microbes
01042 | Copper | Corrosion of household plumbing systems; Erosion of natural deposits; Leaching from wood preservatives
00720 | Cyanide | Discharge from steel/metal factories; Discharge from plastic and fertilizer factories
00951 | Fluoride | Erosion of natural deposits; Water additive which promotes strong teeth; Discharge from fertilizer and aluminum factories
01051 | Lead | Corrosion of household plumbing systems; Erosion of natural deposits
71900 | Mercury | Erosion of natural deposits; Discharge from refineries and factories; Runoff from landfills; Runoff from cropland
00620 | Nitrate | Runoff from fertilizer use; Leaching from septic tanks, sewage; Erosion of natural deposits
00615 | Nitrite | Runoff from fertilizer use; Leaching from septic tanks, sewage; Erosion of natural deposits
01147 | Selenium | Discharge from petroleum and metal refineries; Erosion of natural deposits; Discharge from mines
01059 | Thallium | Leaching from ore-processing sites; Discharge from electronics, glass,and drug factories
03757 | 2,4-D | Runoff from herbicide used on row crops
03614 | 2,4,5-TP | Residue of banned herbicide
38576 | Acrylamide | Added to water during sewage/wastewater treatment
77825 | Alachlor | Runoff from herbicide used on row crops
ATZAZ | Atzazine | Runoff from herbicide used on row crops
03648 | Benzo(a)pyrene | Leaching from linings of water storage tanks and distribution lines
81405 | Carbofuran | Leaching of soil fumigant used on rice and alfalfa
03743 | Chlordane | Residue of banned termiticide
30200 | Dalapon | Runoff from herbicide used on rights of way
DIADIP | Di(2-ethylhexyl)adipate | Discharge from chemical factories
DIPHTH | Di(2-ethylhexyl)phthalate | Discharge from rubber and chemical factories
38437 | Dibromochloropropane | Runoff/leaching from soil fumigant used on soybeans, cotton,pineapples, and orchards
30191 | Dinoseb | Runoff from herbicide used on soybeans and vegetables
04443 | Diquat | Runoff from herbicide use
03767 | Dioxin | Emissions from waste incineration and other combustion; Discharge from chemical factories
38926 | Endothall | Runoff from herbicide use
39390 | Endrin | Residue of banned insecticide
81679 | Epichlorohydrin | Discharge from industrial chemical factories; An impurity of some water treatment chemicals
EDB | Ethylene dibromide | Discharge from petroleum refineries
79743 | Glyphosate | Runoff from herbicide use
39410 | Heptachlor | Residue of banned insecticide
39420 | Heptachlor epoxide | Breakdown of heptachlor
39700 | Hexachlorobenzene | Discharge from metal refineries and agricultural chemical factories
78022 | Hexachlorocyclopent | Discharge from chemical factories
39782 | Lindane | Runoff/leaching from insecticide used on cattle, lumber, gardens
39480 | Methoxychlor | Runoff/leaching from insecticide used on fruits, vegetables, alfalfa, livestock
38865 | Oxamyl | Runoff/leaching from insecticide used on apples, potatoes and tomatoes
39516 | PCBs | Runoff from landfills; Discharge of waste chemicals
39032 | Pentachlorophenol | Discharge from wood preserving factories
39720 | Picloram | Herbicide runoff
39055 | Simazine | Herbicide runoff
39400 | Toxaphene | Runoff/leaching from insecticide used on cotton and cattle
61290 | Benzene | Discharge from factories; Leaching from gas storage tanks and landfills
32102 | Carbon tetrachloride | Discharge from chemical plants and other industrial activities
34301 | Chlorobenzene | Discharge from chemical and agricultural chemical factories
04150 | o-Dichlorobenzene | Discharge from industrial chemical factories
pDCB | p-Dichlorobenzene | Discharge from industrial chemical factories
32103 | 1,2-Dichloroethane | Discharge from industrial chemical factories
34501 | 1,1-Dichloroethylene | Discharge from industrial chemical factories
77093 | cis-1,2-Dichloroethylene | Discharge from industrial chemical factories
1,2-DCE | trans-1,2-Dichloroethylene | Discharge from industrial chemical factories
DCM | Dichloromethane | Discharge from pharmaceutical and chemical factories
34541 | 1,2-Dichloropropane | Discharge from industrial chemical factories
34371 | Ethylbenzene | Discharge from petroleum refineries
HAA5 | HAA5 | By-product of drinking water disinfection
77128 | Styrene | Discharge from rubber and plastic factories; Leaching from landfills
34475 | Tetrachloroethylene | Discharge from factories and dry factories
03684 | 1,2,4-Trichlorobenzene | Discharge from textile-finishing factories
34506 | 1,1,1-Trichloroethane | Discharge from metal degreasing sites and other factories
34511 | 1,1,2-Trichloroethane | Discharge from industrial chemical factories
39180 | Trichloroethylene | Discharge from metal degreasing sites and other factories
82080 | TTHMs | By-product of drinking water disinfection
34010 | Toluene | Discharge from petroleum factories
39175 | Vinyl Chloride | Leaching from PVC piping;Discharge from plastics factories
81551 | Xylenes | Discharge from petroleum factories; Discharge from chemical factories