## Slide 1: Track 2 - Wednesday, 9:00am to 10:15AM
Monthly Data Entry Training
  Making and Saving Layout changes
  Quick Filter
  Troubleshooting data

## Slide 2: Introduction to Statistical Process Control
What is Statistical process control (SPC)?
A method of quality control which uses statistical methods. SPC is applied in order to monitor and control a process. Monitoring and controlling the process ensures that it operates at its full potential thus eliminating waste.
OR
How do I make better beer (Guinness)
OR
How do I produce better product (Water/Wastewater)

## Slide 3: Introduction to Statistical Process Control
If the process has a normal distribution, 99.7% of the population is captured by the curve at three standard deviations from the mean. Stated another way, there is only a 0.3% chance of finding a value beyond 3 standard deviations. Therefore, a measurement value beyond 3 standard deviations indicates that the process has either shifted or become unstable (more variability).
Examples of parameters to look at using SPC:
Effluent Quality Parameters – BOD, TSS, etc..
Finished Water Quality Parameters – Turbidity, Cl2,etc…
Wastewater Process Parameters – MLSS, SRT, F/M
Variance between Process and Lab Results
Benchmarks - Total Operating Cost/Treated Water, BOD Removed / KWH used
….????

## Slide 4: Introduction to Statistical Process Control
Control limits are defined as follows:
Upper Control Limit (UCL) – Average + 3 * Standard Deviation
Upper Warning Limit (UWL) – Average + 2 * Standard Deviation
QC Mean – Average
Lower Warning Limit (UWL) – Average - 2 * Standard Deviation
Lower Control Limit (LCL) – Average - 3 * Standard Deviation
Your initial QC Limits should be calculated
From data when the process was running well
Contains 20 or more data points
Takes into account seasonal changes to process

## Slide 5: Interpreting SPC control charts
All points above or below the Upper and Lower Control Limit
2 Consecutive points are above or below the Warning Limits
7 Consecutive points are on one side of the mean
5 Consecutive points are sloping in one direction
The following rules are derived from the “Western Electric Rules” - “The Western Electric Rules were codified by a specially-appointed committee of the manufacturing division of the Western Electric Company and appeared in the first edition of its Statistical Quality Control Handbook in 1956.[2] Their purpose was to ensure that line workers and engineers interpret control charts in a uniform way” - Wikipedia